## Index
Red5-DHCP — control logic / Sequence of Operations
Generated 2026-08-03 · 109 controllers · 1383 points
Panel | Controller | Equipment | Control strategy | Points | Sheet
LCP-DHC | DDC-DHC-01 | DHC-CHW | Intake valve modulates to CHW setpoint / thermal demand | 10 | DDC-DHC-01
LCP-DHC | DDC-DHC-02 | DHC-STEAM | PRV to 0.2 MPa header + condensate metering | 7 | DDC-DHC-02
LCP-DHC | DDC-DHC-03 | HWT-1 | Level control + makeup | 5 | DDC-DHC-03
LCP-DHC | DDC-DHC-04 | HP-5-1, HP-5-2, HP-3-1 | Level-controlled condensate/kitchen pumps | 21 | DDC-DHC-04
LCP-DHC | DDC-DHC-05 | HP-3-2 | Level-controlled condensate/kitchen pumps | 7 | DDC-DHC-05
LCP-DHC | DDC-DHC-06 | MTR-ELEC-MAIN, MTR-GAS-MAIN, MTR-WATER-MAIN | Energy integration (monitor only) | 3 | DDC-DHC-06
LCP-DHC | DDC-DHC-07 | MTR-DHC-CHW, MTR-DHC-STEAM, MTR-DHC-COND | Energy integration (monitor only) | 3 | DDC-DHC-07
LCP-CT | DDC-CT-01 | CT-1-1, CT-1-2, CT-1 | INV fan cells hold wet-bulb-reset condenser setpoint | 16 | DDC-CT-01
LCP-CT | DDC-CT-02 | CT-2-1, CT-2-2, CT-2 | INV fan cells hold wet-bulb-reset condenser setpoint | 18 | DDC-CT-02
LCP-CT | DDC-CT-03 | CT-3-1, CT-3 | INV fan cells hold wet-bulb-reset condenser setpoint | 11 | DDC-CT-03
LCP-CT | DDC-CT-04 | CDP-1-1, CDP-1-2, CDP-1-3 | Duty/standby with chiller; flow-proof | 12 | DDC-CT-04
LCP-CT | DDC-CT-05 | CDP-2-1, CDP-2-2, CDP-3-1 | Duty/standby with chiller; flow-proof | 12 | DDC-CT-05
LCP-CT | DDC-CT-06 | CDP-3-2 | Duty/standby with chiller; flow-proof | 4 | DDC-CT-06
LCP-CT | DDC-CT-07 | EX-1, EMHX-1, EMHX-2 | Tower free-cooling when wet-bulb low; Emergency DHC HX standby | 9 | DDC-CT-07
LCP-CT | DDC-CT-08 | MTR-CDW-KWH | Energy integration (monitor only) | 1 | DDC-CT-08
LCP-HSL | DDC-HSL-01 | EX-2-1, EX-2-2 | Primary valve modulates to secondary outlet setpoint | 8 | DDC-HSL-01
LCP-HSL | DDC-HSL-02 | CP-1-1, CP-1-2, CP-1-3 | Lead/lag VFD to header Δp (variable flow) | 21 | DDC-HSL-02
LCP-HSL | DDC-HSL-03 | CP-4-1, CP-4-2, CP-5-1 | Lead/lag VFD to header Δp (variable flow) | 21 | DDC-HSL-03
LCP-HSL | DDC-HSL-04 | CP-5-2 | Lead/lag VFD to header Δp (variable flow) | 7 | DDC-HSL-04
LCP-HSL | DDC-HSL-05 | HP-1-1, HP-1-2, HP-1-3 | Heating-season lead/lag to header Δp | 21 | DDC-HSL-05
LCP-HSL | DDC-HSL-06 | EXT-1 | Loop pressurisation | 3 | DDC-HSL-06
LCP-HSL | DDC-HSL-07 | ST-1 | OA tempering to setpoint | 3 | DDC-HSL-07
LCP-HSL | DDC-HSL-08 | AC-1, AC-2, AC-3 | Schedule + SAT coil control + economizer | 29 | DDC-HSL-08
LCP-HSL | DDC-HSL-09 | AC-4, AC-5, AC-6 | Schedule + SAT coil control + economizer | 34 | DDC-HSL-09
LCP-HSL | DDC-HSL-10 | AC-26 | Schedule + SAT coil control + economizer | 12 | DDC-HSL-10
LCP-HSL | DDC-HSL-11 | FCU-L-N, FCU-L-NE, FCU-L-SE | Zone thermostat + schedule batch | 21 | DDC-HSL-11
LCP-HSL | DDC-HSL-12 | FCU-L-S, FCU-L-SW | Zone thermostat + schedule batch | 14 | DDC-HSL-12
LCP-HSL | DDC-HSL-13 | SF-6, EF-28, EF-32 | Scheduled ventilation / exhaust | 9 | DDC-HSL-13
LCP-HSL | DDC-HSL-14 | EF-33, EF-97, RF-7 | Scheduled ventilation / exhaust; Start/stop + status/alarm | 9 | DDC-HSL-14
LCP-HSL | DDC-HSL-15 | RF-8, RF-9 | Start/stop + status/alarm | 6 | DDC-HSL-15
LCP-HSL | DDC-HSL-16 | POOL-FP | Start/stop + status/alarm | 3 | DDC-HSL-16
LCP-HSL | DDC-HSL-17 | MTR-AHU-KWH | Energy integration (monitor only) | 1 | DDC-HSL-17
LCP-HSH | DDC-HSH-01 | EX-3-1, EX-3-2 | Primary valve modulates to secondary outlet setpoint | 8 | DDC-HSH-01
LCP-HSH | DDC-HSH-02 | CP-2-1, CP-2-2, CP-2-3 | Lead/lag VFD to header Δp (variable flow) | 21 | DDC-HSH-02
LCP-HSH | DDC-HSH-03 | CP-3-1, CP-3-2, CP-6-1 | Lead/lag VFD to header Δp (variable flow) | 21 | DDC-HSH-03
LCP-HSH | DDC-HSH-04 | CP-6-2 | Lead/lag VFD to header Δp (variable flow) | 7 | DDC-HSH-04
LCP-HSH | DDC-HSH-05 | HP-2-1, HP-2-2, HP-2-3 | Heating-season lead/lag to header Δp | 21 | DDC-HSH-05
LCP-HSH | DDC-HSH-06 | EXT-2 | Loop pressurisation | 3 | DDC-HSH-06
LCP-HSH | DDC-HSH-07 | ST-2 | OA tempering to setpoint | 3 | DDC-HSH-07
LCP-HSH | DDC-HSH-08 | EVU-11, EVU-12, EVU-13 | Scheduled ventilation / exhaust | 39 | DDC-HSH-08
LCP-HSH | DDC-HSH-09 | EVU-14, EVU-15 | Scheduled ventilation / exhaust | 24 | DDC-HSH-09
LCP-HSH | DDC-HSH-10 | FCU-H-N, FCU-H-NE, FCU-H-SE | Zone thermostat + schedule batch | 21 | DDC-HSH-10
LCP-HSH | DDC-HSH-11 | FCU-H-S, FCU-H-SW | Zone thermostat + schedule batch | 14 | DDC-HSH-11
LCP-3637 | DDC-3637-01 | R-1 | Economic dispatch + CHW/CW reset + twin-screw staging | 10 | DDC-3637-01
LCP-3637 | DDC-3637-02 | HEX-1 | Primary valve modulates to secondary outlet setpoint | 7 | DDC-3637-02
LCP-3637 | DDC-3637-03 | CP-7-1, CP-7-2, CP-8-1 | Lead/lag VFD to header Δp (variable flow) | 21 | DDC-3637-03
LCP-3637 | DDC-3637-04 | CP-8-2, CP-8-3 | Lead/lag VFD to header Δp (variable flow) | 14 | DDC-3637-04
LCP-3637 | DDC-3637-05 | HP-4-1, HP-4-2 | Buffer-loop lead/lag to Δp | 14 | DDC-3637-05
LCP-3637 | DDC-3637-06 | EX4, EXT-3 | Primary valve modulates to secondary outlet setpoint; Loop pressurisation | 7 | DDC-3637-06
LCP-3637 | DDC-3637-07 | CHGV-1, CHGV-2 | Bumpless source transfer + flow proof | 4 | DDC-3637-07
LCP-3637 | DDC-3637-08 | AC-22, AC-23, AC-24 | Schedule + SAT coil control + economizer | 38 | DDC-3637-08
LCP-3637 | DDC-3637-09 | AC-25, AC-27 | Schedule + SAT coil control + economizer | 26 | DDC-3637-09
LCP-3637 | DDC-3637-10 | FCU-3637 | Zone thermostat + schedule batch | 7 | DDC-3637-10
LCP-3637 | DDC-3637-11 | EF-82, EF-83, EF-84 | Scheduled ventilation / exhaust | 11 | DDC-3637-11
LCP-3637 | DDC-3637-12 | EF-85, EF-86, EF-89 | Scheduled ventilation / exhaust | 9 | DDC-3637-12
LCP-3637 | DDC-3637-13 | EF-98 | Scheduled ventilation / exhaust | 3 | DDC-3637-13
LCP-1F | DDC-1F-01 | AC-7 | Schedule + SAT coil control + economizer | 12 | DDC-1F-01
LCP-1F | DDC-1F-02 | EVU-1, EVU-2, EVU-3 | Scheduled ventilation / exhaust | 36 | DDC-1F-02
LCP-1F | DDC-1F-03 | EF-41, EF-42 | Scheduled ventilation / exhaust | 6 | DDC-1F-03
LCP-2F | DDC-2F-01 | AC-8, AC-9, AC-10 | Schedule + SAT coil control + economizer | 36 | DDC-2F-01
LCP-2F | DDC-2F-02 | AC-11, AC-12, AC-13 | Schedule + SAT coil control + economizer | 39 | DDC-2F-02
LCP-2F | DDC-2F-03 | EVU-4, EVU-5, EVU-6 | Scheduled ventilation / exhaust | 36 | DDC-2F-03
LCP-2F | DDC-2F-04 | EF-2-1, EF-46, EF-47 | Scheduled ventilation / exhaust | 9 | DDC-2F-04
LCP-3F | DDC-3F-01 | AC-14, AC-15, AC-16 | Schedule + SAT coil control + economizer | 38 | DDC-3F-01
LCP-3F | DDC-3F-02 | EVU-7 | Scheduled ventilation / exhaust | 12 | DDC-3F-02
LCP-3F | DDC-3F-03 | EF-56, EF-60, EF-61 | Scheduled ventilation / exhaust | 9 | DDC-3F-03
LCP-3F | DDC-3F-04 | EF-62, EF-76, EF-77 | Scheduled ventilation / exhaust | 9 | DDC-3F-04
LCP-4F | DDC-4F-01 | AC-17, AC-18, AC-19 | Schedule + SAT coil control + economizer | 38 | DDC-4F-01
LCP-4F | DDC-4F-02 | AC-20, AC-21 | Schedule + SAT coil control + economizer | 24 | DDC-4F-02
LCP-4F | DDC-4F-03 | EVU-8, EVU-9, EVU-10 | Scheduled ventilation / exhaust | 39 | DDC-4F-03
LCP-4F | DDC-4F-04 | EF-54, EF-55, EF-57 | Scheduled ventilation / exhaust | 9 | DDC-4F-04
LCP-4F | DDC-4F-05 | EF-58, EF-59, EF-59-2 | Scheduled ventilation / exhaust | 9 | DDC-4F-05
LCP-4F | DDC-4F-06 | EF-67, EF-69, EF-70 | Scheduled ventilation / exhaust | 11 | DDC-4F-06
LCP-4F | DDC-4F-07 | EF-71 | Scheduled ventilation / exhaust | 3 | DDC-4F-07
LCP-PKG | DDC-PKG-01 | PAC-1-1, PAC-1-2, PAC-2 | Enable/monitor; integral DX (some 24/7) | 9 | DDC-PKG-01
LCP-PKG | DDC-PKG-02 | PAC-3, PAC-4, PAC-5 | Enable/monitor; integral DX (some 24/7) | 9 | DDC-PKG-02
LCP-PKG | DDC-PKG-03 | PCU-1-1, PCU-1-2, PCU-5 | Enable/monitor; integral DX (some 24/7) | 9 | DDC-PKG-03
LCP-PKG | DDC-PKG-04 | PCU-6, PCU-7, PCU-8 | Enable/monitor; integral DX (some 24/7) | 9 | DDC-PKG-04
LCP-PKG | DDC-PKG-05 | PCU-10, PCU-11, PCU-12 | Enable/monitor; integral DX (some 24/7) | 9 | DDC-PKG-05
LCP-PKG | DDC-PKG-06 | PCU-13, PMAC-1 | Enable/monitor; integral DX (some 24/7) | 6 | DDC-PKG-06
LCP-PKG | DDC-PKG-07 | REFR-1 | Start/stop + status/alarm | 7 | DDC-PKG-07
LCP-LTG | DDC-LTG-01 | LTG-AVIATION, LTG-NEON, LTG-BALCONY-L | Time/astro On-Off + status | 6 | DDC-LTG-01
LCP-LTG | DDC-LTG-02 | LTG-BALCONY-H, LTG-CORRIDOR, LTG-LOBBY | Time/astro On-Off + status | 6 | DDC-LTG-02
LCP-LTG | DDC-LTG-03 | LTG-SOFFIT, LTG-TENANT | Time/astro On-Off + status | 4 | DDC-LTG-03
LCP-DHW | DDC-DHW-01 | DHW-1, DHW-2, DHW-3 | Steam charging to storage setpoint + Legionella cycle | 21 | DDC-DHW-01
LCP-DHW | DDC-DHW-02 | DHW-4 | Steam charging to storage setpoint + Legionella cycle | 7 | DDC-DHW-02
LCP-SAN | DDC-SAN-01 | MP-1, MP-2, MP-3 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-01
LCP-SAN | DDC-SAN-02 | MP-4, P-1, P-2 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-02
LCP-SAN | DDC-SAN-03 | P-3, P-4, P-5 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-03
LCP-SAN | DDC-SAN-04 | P-6, RCVT-1, ELVT-1 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-04
LCP-SAN | DDC-SAN-05 | REUSET-1, FIRET-1, DP-1 | Lead/lag booster + float-level sump/sewage | 8 | DDC-SAN-05
LCP-SAN | DDC-SAN-06 | DP-2, DP-3, DP-4 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-06
LCP-SAN | DDC-SAN-07 | DP-5, DP-6, DP-7 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-07
LCP-SAN | DDC-SAN-08 | DP-8, DP-9, DP-10 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-08
LCP-SAN | DDC-SAN-09 | DP-11, DP-12, DP-13 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-09
LCP-SAN | DDC-SAN-10 | DP-14, BL-1-1, BL-1-2 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-10
LCP-SAN | DDC-SAN-11 | BL-2-1, BL-2-2, BL-F-1 | Lead/lag booster + float-level sump/sewage | 9 | DDC-SAN-11
LCP-SAN | DDC-SAN-12 | BL-F-2 | Lead/lag booster + float-level sump/sewage | 3 | DDC-SAN-12
LCP-FILT | DDC-FILT-01 | FILT-BATHM, FILT-BATHW, FILT-SAUNA | Scheduled circulation + backwash | 9 | DDC-FILT-01
LCP-FILT | DDC-FILT-02 | FILT-SAUNAC, FILT-OTAKI, FILT-UNKAI | Scheduled circulation + backwash | 9 | DDC-FILT-02
LCP-FILT | DDC-FILT-03 | FILT-FOUNT, FILT-RAIN | Scheduled circulation + backwash | 6 | DDC-FILT-03
LCP-SMK | DDC-SMK-01 | SMF-1, SMF-2, SMF-3 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-01
LCP-SMK | DDC-SMK-02 | SMF-4, SMF-5, SMF-6 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-02
LCP-SMK | DDC-SMK-03 | SMF-7, SMF-8, SMF-9 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-03
LCP-SMK | DDC-SMK-04 | SMF-10, SMF-11, SMF-12 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-04
LCP-SMK | DDC-SMK-05 | SMF-13, SMF-14, SMF-15 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-05
LCP-SMK | DDC-SMK-06 | SMF-16, SMF-17, SMF-18 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-06
LCP-SMK | DDC-SMK-07 | SMF-19, SMF-20, SMF-21 | Hard-wired fire start; BMS monitors + smoke-mode | 9 | DDC-SMK-07
LCP-SMK | DDC-SMK-08 | SMF-22, SMK-FIRE | Hard-wired fire start; BMS monitors + smoke-mode | 4 | DDC-SMK-08

## DDC-DHC-01
Control logic — DDC-DHC-01
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: DHC-CHW
Strategy: Intake valve modulates to CHW setpoint / thermal demand
Sequence of Operations
Purpose
• Primary cooling source: modulate the DHC intake so the building CHW header / thermal demand is met at minimum district energy + demand cost.
Control
• Modulate intake control valve `DHC-CHW.CV` (feedback `DHC-CHW.CVFB`) to hold the CHW supply setpoint on `DHC-CHW.CS-T` (return `DHC-CHW.CR-T`); cap opening during the district peak window.
• Meter thermal energy `DHC-CHW.GJ` and flow `DHC-CHW.FLW` for demand limiting; coordinate changeover with R-1 (CHGV-1/2).
Safeties & monitoring
• High/low supply-temp and header-pressure alarms (`DHC-CHW.CS-T`, `DHC-CHW.CS-P`); low-flow / valve-fault supervision; open the valve on loss of BMS (fail-safe cooling).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DHC-CHW.CS-T | AI | Supply (CS) temp | 4-20mA | °C |  | Y
DHC-CHW.CR-T | AI | Return (CR) temp | 4-20mA | °C
DHC-CHW.CS-P | AI | Supply header pressure | 4-20mA | MPa |  | Y
DHC-CHW.CR-P | AI | Return header pressure | 4-20mA | MPa
DHC-CHW.FLW | AI | Intake flow | 4-20mA | m³/h
DHC-CHW.GJ | AI | Thermal-energy meter | Pulse/Modbus | GJ
DHC-CHW.CV | AO | Intake control valve | 0-10V | % | Y
DHC-CHW.CVFB | AI | Intake valve position fb | 4-20mA | %
DHC-CHW.ISOL | BO | Intake isolation valve open/close | DO relay | - | Y
DHC-CHW.ISOL-ST | BI | Isolation valve status | DI dry contact | - |  | Y

## DDC-DHC-02
Control logic — DDC-DHC-02
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: DHC-STEAM
Strategy: PRV to 0.2 MPa header + condensate metering
Sequence of Operations
Purpose
• DHC steam intake: reduce 0.8 MPa district steam to the 0.2 MPa house header and meter mass flow + condensate return.
Control
• PRV holds the 0.2 MPa header setpoint; meter steam mass `DHC-STEAM.MASS` and condensate hot-return `DHC-STEAM.HR-M` back to the hot-well.
• Enable in heating season only; isolate and drain in cooling season (Apr–May off).
Safeties
• Over-pressure relief, high-header-pressure alarm, condensate-level and trap supervision.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DHC-STEAM.SS-P | AI | Supply (SS 8k) pressure | 4-20mA | MPa |  | Y
DHC-STEAM.MASS | AI | Steam mass-flow meter | Pulse/Modbus | t/h
DHC-STEAM.PRV | AO | PRV 8k->2k reducing valve | 0-10V | % | Y
DHC-STEAM.SSH2-P | AI | Reduced (SSH 2k) pressure | 4-20mA | MPa
DHC-STEAM.ISOL | BO | Main isolation valve open/close | DO relay | - | Y
DHC-STEAM.ISOL-ST | BI | Isolation valve status | DI dry contact | - |  | Y
DHC-STEAM.HR-M | AI | Condensate (HR) return meter | Pulse/Modbus | L

## DDC-DHC-03
Control logic — DDC-DHC-03
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: HWT-1
Strategy: Level control + makeup
Sequence of Operations
Purpose
• Hot-well / condensate tank: buffer condensate return to the district.
Control
• Level control with makeup; high/low-level alarms.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HWT-1.LVL | AI | Tank level | 4-20mA | % |  | Y
HWT-1.HI | BI | High-level alarm | DI dry contact | - |  | Y
HWT-1.LO | BI | Low-level alarm | DI dry contact | - |  | Y
HWT-1.T | AI | Condensate temp | 4-20mA | °C
HWT-1.MU | BO | Make-up water valve | DO relay | -

## DDC-DHC-04
Control logic — DDC-DHC-04
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: HP-5-1, HP-5-2, HP-3-1
Strategy: Level-controlled condensate/kitchen pumps
Sequence of Operations
Purpose
• Hot-well / condensate-return pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `HP-5-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (HP-5-1, HP-5-2, HP-3-1): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the hot-well level; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HP-5-1.RUN | BI | Run status | DI dry contact | -
HP-5-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-5-1.SS | BO | Start/Stop command | DO relay | -
HP-5-1.SPD | AO | VFD speed command | 0-10V | % | Y
HP-5-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-5-1.KW | AI | Power | 4-20mA | kW
HP-5-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-5-2.RUN | BI | Run status | DI dry contact | -
HP-5-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-5-2.SS | BO | Start/Stop command | DO relay | -
HP-5-2.SPD | AO | VFD speed command | 0-10V | % | Y
HP-5-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-5-2.KW | AI | Power | 4-20mA | kW
HP-5-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-3-1.RUN | BI | Run status | DI dry contact | -
HP-3-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-3-1.SS | BO | Start/Stop command | DO relay | -
HP-3-1.SPD | AO | VFD speed command | 0-10V | % | Y
HP-3-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-3-1.KW | AI | Power | 4-20mA | kW
HP-3-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-DHC-05
Control logic — DDC-DHC-05
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: HP-3-2
Strategy: Level-controlled condensate/kitchen pumps
Sequence of Operations
Purpose
• Hot-well / condensate-return pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `HP-3-2.SS`.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the hot-well level; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HP-3-2.RUN | BI | Run status | DI dry contact | -
HP-3-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-3-2.SS | BO | Start/Stop command | DO relay | -
HP-3-2.SPD | AO | VFD speed command | 0-10V | % | Y
HP-3-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-3-2.KW | AI | Power | 4-20mA | kW
HP-3-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-DHC-06
Control logic — DDC-DHC-06
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: MTR-ELEC-MAIN, MTR-GAS-MAIN, MTR-WATER-MAIN
Strategy: Energy integration (monitor only)
Sequence of Operations
Purpose
• Energy metering (no control output).
Function
• Integrate pulse/analog energy for trend, demand limiting and peak monitoring; feed the dispatch/peak-shave logic.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
MTR-ELEC-MAIN | AI | Main electricity (kWh) | Pulse/Modbus | kWh
MTR-GAS-MAIN | AI | City gas (m³) | Pulse/Modbus | m³
MTR-WATER-MAIN | AI | City water (m³) | Pulse/Modbus | m³

## DDC-DHC-07
Control logic — DDC-DHC-07
Panel LCP-DHC (DHC intake & hot-well panel) · B2F Machine Room
Equipment: MTR-DHC-CHW, MTR-DHC-STEAM, MTR-DHC-COND
Strategy: Energy integration (monitor only)
Sequence of Operations
Purpose
• Energy metering (no control output).
Function
• Integrate pulse/analog energy for trend, demand limiting and peak monitoring; feed the dispatch/peak-shave logic.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
MTR-DHC-CHW | AI | DHC chilled-water energy (受入) | Pulse/Modbus | GJ
MTR-DHC-STEAM | AI | DHC steam energy (受入) | Pulse/Modbus | t/h
MTR-DHC-COND | AI | DHC condensate return (HR) | Pulse/Modbus | L

## DDC-CT-01
Control logic — DDC-CT-01
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: CT-1-1, CT-1-2, CT-1
Strategy: INV fan cells hold wet-bulb-reset condenser setpoint
Sequence of Operations
Purpose
• Reject condenser heat and hold the condenser-water setpoint at minimum fan energy.
Staging & reset
• Condenser-water setpoint = wet-bulb + approach, floored for chiller min-lift.
• INV fan cells `*.SPD` (feedback `*.SPDFB`) modulate together to hold setpoint; stage cells (CT-1-1, CT-1-2) as load rises; start/stop `*.SS`.
• Sequence with condenser pumps + chiller; run only when the chiller/free-cooling calls.
Safeties & monitoring
• Basin E/H heater on low temp (freeze); makeup/level & conductivity (blowdown, Legionella control); fan INV fault `*.TRIP`; run status `*.RUN`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CT-1-1.RUN | BI | Fan run status | DI dry contact | -
CT-1-1.TRIP | BI | Fan INV fault | DI dry contact | - |  | Y
CT-1-1.SS | BO | Fan start/stop | DO relay | -
CT-1-1.SPD | AO | Fan VFD speed command | 0-10V | % | Y
CT-1-1.SPDFB | AI | Fan speed feedback | 4-20mA | %
CT-1-2.RUN | BI | Fan run status | DI dry contact | -
CT-1-2.TRIP | BI | Fan INV fault | DI dry contact | - |  | Y
CT-1-2.SS | BO | Fan start/stop | DO relay | -
CT-1-2.SPD | AO | Fan VFD speed command | 0-10V | % | Y
CT-1-2.SPDFB | AI | Fan speed feedback | 4-20mA | %
CT-1.LVL | AI | Basin water level | 4-20mA | % |  | Y
CT-1.MU | BO | Make-up water valve | DO relay | -
CT-1.BLD | BO | Bleed/blowdown valve | DO relay | -
CT-1.DRY | BI | Low-water (渇水) alarm | DI dry contact | - |  | Y
CT-1.CHEM | BI | Chemical dosing (薬注) batch fault | DI dry contact | - |  | Y
CT-1.EH | BO | Basin heater (E/H) enable | DO relay | -

## DDC-CT-02
Control logic — DDC-CT-02
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: CT-2-1, CT-2-2, CT-2
Strategy: INV fan cells hold wet-bulb-reset condenser setpoint
Sequence of Operations
Purpose
• Reject condenser heat and hold the condenser-water setpoint at minimum fan energy.
Staging & reset
• Condenser-water setpoint = wet-bulb + approach, floored for chiller min-lift.
• INV fan cells `*.SPD` (feedback `*.SPDFB`) modulate together to hold setpoint; stage cells (CT-2-1, CT-2-2) as load rises; start/stop `*.SS`.
• Sequence with condenser pumps + chiller; run only when the chiller/free-cooling calls.
Safeties & monitoring
• Basin E/H heater on low temp (freeze); makeup/level & conductivity (blowdown, Legionella control); fan INV fault `*.TRIP`; run status `*.RUN`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CT-2-1.RUN | BI | Fan run status | DI dry contact | -
CT-2-1.TRIP | BI | Fan INV fault | DI dry contact | - |  | Y
CT-2-1.SS | BO | Fan start/stop | DO relay | -
CT-2-1.SPD | AO | Fan VFD speed command | 0-10V | % | Y
CT-2-1.SPDFB | AI | Fan speed feedback | 4-20mA | %
CT-2-2.RUN | BI | Fan run status | DI dry contact | -
CT-2-2.TRIP | BI | Fan INV fault | DI dry contact | - |  | Y
CT-2-2.SS | BO | Fan start/stop | DO relay | -
CT-2-2.SPD | AO | Fan VFD speed command | 0-10V | % | Y
CT-2-2.SPDFB | AI | Fan speed feedback | 4-20mA | %
CT-2.LVL | AI | Basin water level | 4-20mA | % |  | Y
CT-2.MU | BO | Make-up water valve | DO relay | -
CT-2.BLD | BO | Bleed/blowdown valve | DO relay | -
CT-2.DRY | BI | Low-water (渇水) alarm | DI dry contact | - |  | Y
CT-2.CHEM | BI | Chemical dosing (薬注) batch fault | DI dry contact | - |  | Y
CT-2.EH | BO | Basin heater (E/H) enable | DO relay | -
CT-2.FILT-RUN | BI | Filtration (ろ過) pump run | DI dry contact | -
CT-2.FILT-SS | BO | Filtration pump start/stop | DO relay | -

## DDC-CT-03
Control logic — DDC-CT-03
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: CT-3-1, CT-3
Strategy: INV fan cells hold wet-bulb-reset condenser setpoint
Sequence of Operations
Purpose
• Reject condenser heat and hold the condenser-water setpoint at minimum fan energy.
Staging & reset
• Condenser-water setpoint = wet-bulb + approach, floored for chiller min-lift.
• INV fan cells `*.SPD` (feedback `*.SPDFB`) modulate together to hold setpoint; stage cells (CT-3-1) as load rises; start/stop `*.SS`.
• Sequence with condenser pumps + chiller; run only when the chiller/free-cooling calls.
Safeties & monitoring
• Basin E/H heater on low temp (freeze); makeup/level & conductivity (blowdown, Legionella control); fan INV fault `*.TRIP`; run status `*.RUN`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CT-3-1.RUN | BI | Fan run status | DI dry contact | -
CT-3-1.TRIP | BI | Fan INV fault | DI dry contact | - |  | Y
CT-3-1.SS | BO | Fan start/stop | DO relay | -
CT-3-1.SPD | AO | Fan VFD speed command | 0-10V | % | Y
CT-3-1.SPDFB | AI | Fan speed feedback | 4-20mA | %
CT-3.LVL | AI | Basin water level | 4-20mA | % |  | Y
CT-3.MU | BO | Make-up water valve | DO relay | -
CT-3.BLD | BO | Bleed/blowdown valve | DO relay | -
CT-3.DRY | BI | Low-water (渇水) alarm | DI dry contact | - |  | Y
CT-3.CHEM | BI | Chemical dosing (薬注) batch fault | DI dry contact | - |  | Y
CT-3.EH | BO | Basin heater (E/H) enable | DO relay | -

## DDC-CT-04
Control logic — DDC-CT-04
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: CDP-1-1, CDP-1-2, CDP-1-3
Strategy: Duty/standby with chiller; flow-proof
Sequence of Operations
Purpose
• Condenser-water pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CDP-1-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CDP-1-1, CDP-1-2, CDP-1-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• Constant-speed; maintain header differential pressure via staging and the min-flow bypass.
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CDP-1-1.RUN | BI | Run status | DI dry contact | -
CDP-1-1.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-1-1.SS | BO | Start/Stop command | DO relay | -
CDP-1-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CDP-1-2.RUN | BI | Run status | DI dry contact | -
CDP-1-2.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-1-2.SS | BO | Start/Stop command | DO relay | -
CDP-1-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CDP-1-3.RUN | BI | Run status | DI dry contact | -
CDP-1-3.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-1-3.SS | BO | Start/Stop command | DO relay | -
CDP-1-3.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-CT-05
Control logic — DDC-CT-05
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: CDP-2-1, CDP-2-2, CDP-3-1
Strategy: Duty/standby with chiller; flow-proof
Sequence of Operations
Purpose
• Condenser-water pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CDP-2-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CDP-2-1, CDP-2-2, CDP-3-1): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• Constant-speed; maintain header differential pressure via staging and the min-flow bypass.
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CDP-2-1.RUN | BI | Run status | DI dry contact | -
CDP-2-1.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-2-1.SS | BO | Start/Stop command | DO relay | -
CDP-2-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CDP-2-2.RUN | BI | Run status | DI dry contact | -
CDP-2-2.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-2-2.SS | BO | Start/Stop command | DO relay | -
CDP-2-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CDP-3-1.RUN | BI | Run status | DI dry contact | -
CDP-3-1.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-3-1.SS | BO | Start/Stop command | DO relay | -
CDP-3-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-CT-06
Control logic — DDC-CT-06
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: CDP-3-2
Strategy: Duty/standby with chiller; flow-proof
Sequence of Operations
Purpose
• Condenser-water pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CDP-3-2.SS`.
Modulation & reset
• Constant-speed; maintain header differential pressure via staging and the min-flow bypass.
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CDP-3-2.RUN | BI | Run status | DI dry contact | -
CDP-3-2.TRIP | BI | Fault / breaker trip | DI dry contact | - |  | Y
CDP-3-2.SS | BO | Start/Stop command | DO relay | -
CDP-3-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-CT-07
Control logic — DDC-CT-07
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: EX-1, EMHX-1, EMHX-2
Strategy: Tower free-cooling when wet-bulb low; Emergency DHC HX standby
Sequence of Operations
[Winter free-cooling heat exchanger] — EX-1
Purpose
• Winter/shoulder free-cooling: use the cooling tower to make chilled water via the HX when wet-bulb is low enough, displacing the chiller.
Control
• Enable when tower-approachable CHW temp < CHW setpoint; modulate the primary valve to hold the loop setpoint; hand over to/from mechanical cooling with hysteresis.
Safeties
• Freeze protection; isolate when disabled.
[Emergency cooling heat exchanger] — EMHX-1, EMHX-2
Purpose
• Transfer heat to the emergency DHC loop; hold the secondary supply temperature.
Control
• Modulate primary control valve `*.PV` (feedback `*.PVFB`) to hold the secondary outlet setpoint `*.S-OUT` from primary inlet `*.P-IN`.
• Lead/lag/standby across 2 exchangers (EMHX-1, EMHX-2): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Safeties
• Freeze / high-temp limit on the secondary; valve-fault supervision; isolate on served-loop shutdown.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EX-1.EN | BO | Free-cooling enable / changeover | DO relay | - | Y
EX-1.ST | AI | CHW-side leaving temp | 4-20mA | °C
EX-1.CV | AO | CW-side control valve | 0-10V | % | Y
EMHX-1.EN | BO | Emergency cooling enable | DO relay | - | Y
EMHX-1.ST | AI | Cooling-water leaving temp | 4-20mA | °C
EMHX-1.ISOL | BO | DHC-side isolation valve | DO relay | -
EMHX-2.EN | BO | Emergency cooling enable | DO relay | - | Y
EMHX-2.ST | AI | Cooling-water leaving temp | 4-20mA | °C
EMHX-2.ISOL | BO | DHC-side isolation valve | DO relay | -

## DDC-CT-08
Control logic — DDC-CT-08
Panel LCP-CT (Cooling-tower & condenser-water panel) · Rooftop / PH
Equipment: MTR-CDW-KWH
Strategy: Energy integration (monitor only)
Sequence of Operations
Purpose
• Energy metering (no control output).
Function
• Integrate pulse/analog energy for trend, demand limiting and peak monitoring; feed the dispatch/peak-shave logic.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
MTR-CDW-KWH | AI | Cooling-tower/condenser sub-meter | Pulse/Modbus | kWh

## DDC-HSL-01
Control logic — DDC-HSL-01
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: EX-2-1, EX-2-2
Strategy: Primary valve modulates to secondary outlet setpoint
Sequence of Operations
Purpose
• Transfer heat to the tempered loop; hold the secondary supply temperature.
Control
• Modulate primary control valve `*.PV` (feedback `*.PVFB`) to hold the secondary outlet setpoint `*.S-OUT` from primary inlet `*.P-IN`.
• Lead/lag/standby across 2 exchangers (EX-2-1, EX-2-2): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Safeties
• Freeze / high-temp limit on the secondary; valve-fault supervision; isolate on served-loop shutdown.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EX-2-1.P-IN | AI | Primary inlet temp (laundry) | 4-20mA | °C
EX-2-1.S-OUT | AI | Secondary outlet (supply) temp | 4-20mA | °C | Y | Y
EX-2-1.PV | AO | Primary control valve | 0-10V | % | Y
EX-2-1.PVFB | AI | Primary valve position fb | 4-20mA | %
EX-2-2.P-IN | AI | Primary inlet temp (laundry) | 4-20mA | °C
EX-2-2.S-OUT | AI | Secondary outlet (supply) temp | 4-20mA | °C | Y | Y
EX-2-2.PV | AO | Primary control valve | 0-10V | % | Y
EX-2-2.PVFB | AI | Primary valve position fb | 4-20mA | %

## DDC-HSL-02
Control logic — DDC-HSL-02
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: CP-1-1, CP-1-2, CP-1-3
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-1-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CP-1-1, CP-1-2, CP-1-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-1-1.RUN | BI | Run status | DI dry contact | -
CP-1-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-1-1.SS | BO | Start/Stop command | DO relay | -
CP-1-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-1-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-1-1.KW | AI | Power | 4-20mA | kW
CP-1-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-1-2.RUN | BI | Run status | DI dry contact | -
CP-1-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-1-2.SS | BO | Start/Stop command | DO relay | -
CP-1-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-1-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-1-2.KW | AI | Power | 4-20mA | kW
CP-1-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-1-3.RUN | BI | Run status | DI dry contact | -
CP-1-3.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-1-3.SS | BO | Start/Stop command | DO relay | -
CP-1-3.SPD | AO | VFD speed command | 0-10V | % | Y
CP-1-3.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-1-3.KW | AI | Power | 4-20mA | kW
CP-1-3.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSL-03
Control logic — DDC-HSL-03
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: CP-4-1, CP-4-2, CP-5-1
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-4-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CP-4-1, CP-4-2, CP-5-1): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-4-1.RUN | BI | Run status | DI dry contact | -
CP-4-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-4-1.SS | BO | Start/Stop command | DO relay | -
CP-4-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-4-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-4-1.KW | AI | Power | 4-20mA | kW
CP-4-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-4-2.RUN | BI | Run status | DI dry contact | -
CP-4-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-4-2.SS | BO | Start/Stop command | DO relay | -
CP-4-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-4-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-4-2.KW | AI | Power | 4-20mA | kW
CP-4-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-5-1.RUN | BI | Run status | DI dry contact | -
CP-5-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-5-1.SS | BO | Start/Stop command | DO relay | -
CP-5-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-5-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-5-1.KW | AI | Power | 4-20mA | kW
CP-5-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSL-04
Control logic — DDC-HSL-04
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: CP-5-2
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-5-2.SS`.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-5-2.RUN | BI | Run status | DI dry contact | -
CP-5-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-5-2.SS | BO | Start/Stop command | DO relay | -
CP-5-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-5-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-5-2.KW | AI | Power | 4-20mA | kW
CP-5-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSL-05
Control logic — DDC-HSL-05
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: HP-1-1, HP-1-2, HP-1-3
Strategy: Heating-season lead/lag to header Δp
Sequence of Operations
Purpose
• Hot-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `HP-1-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (HP-1-1, HP-1-2, HP-1-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HP-1-1.RUN | BI | Run status | DI dry contact | -
HP-1-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-1-1.SS | BO | Start/Stop command | DO relay | -
HP-1-1.SPD | AO | VFD speed command | 0-10V | % | Y
HP-1-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-1-1.KW | AI | Power | 4-20mA | kW
HP-1-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-1-2.RUN | BI | Run status | DI dry contact | -
HP-1-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-1-2.SS | BO | Start/Stop command | DO relay | -
HP-1-2.SPD | AO | VFD speed command | 0-10V | % | Y
HP-1-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-1-2.KW | AI | Power | 4-20mA | kW
HP-1-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-1-3.RUN | BI | Run status | DI dry contact | -
HP-1-3.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-1-3.SS | BO | Start/Stop command | DO relay | -
HP-1-3.SPD | AO | VFD speed command | 0-10V | % | Y
HP-1-3.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-1-3.KW | AI | Power | 4-20mA | kW
HP-1-3.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSL-06
Control logic — DDC-HSL-06
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: EXT-1
Strategy: Loop pressurisation
Sequence of Operations
Purpose
• Loop pressurisation / expansion set.
Control
• Maintain fill pressure via makeup valve/pump; low-pressure & level alarms.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EXT-1.LVL | AI | Tank level | 4-20mA | % |  | Y
EXT-1.HI | BI | High-level alarm | DI dry contact | - |  | Y
EXT-1.LO | BI | Low-level alarm | DI dry contact | - |  | Y

## DDC-HSL-07
Control logic — DDC-HSL-07
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: ST-1
Strategy: OA tempering to setpoint
Sequence of Operations
Purpose
• Outdoor-air station: temper and deliver ventilation air to the loop.
Control
• Modulate to the OA supply setpoint; enable with the served distribution; economizer-favourable in shoulder season.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
ST-1.T | AI | Outdoor dry-bulb temp | 4-20mA | °C
ST-1.RH | AI | Outdoor humidity | 4-20mA | %RH
ST-1.WB | AI | Wet-bulb temp (計測/演算) | 4-20mA | °C

## DDC-HSL-08
Control logic — DDC-HSL-08
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: AC-1, AC-2, AC-3
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-1, AC-2, AC-3: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• Constant-volume supply fan (fixed speed).
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-1.RUN | BI | Supply fan run status | DI dry contact | -
AC-1.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-1.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-1.SPD | AO | Supply fan speed (fixed) | 0-10V | %
AC-1.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-1.RAT | AI | Return air temp | 4-20mA | °C
AC-1.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-1.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-1.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-1.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-1.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-2.RUN | BI | Supply fan run status | DI dry contact | -
AC-2.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-2.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-2.SPD | AO | Supply fan speed (fixed) | 0-10V | %
AC-2.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-2.RAT | AI | Return air temp | 4-20mA | °C
AC-2.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-2.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-2.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-3.RUN | BI | Supply fan run status | DI dry contact | -
AC-3.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-3.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-3.SPD | AO | Supply fan speed (fixed) | 0-10V | %
AC-3.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-3.RAT | AI | Return air temp | 4-20mA | °C
AC-3.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-3.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-3.OAD | AO | Outdoor-air damper | 0-10V | % | Y

## DDC-HSL-09
Control logic — DDC-HSL-09
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: AC-4, AC-5, AC-6
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-4, AC-5, AC-6: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-4.RUN | BI | Supply fan run status | DI dry contact | -
AC-4.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-4.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-4.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-4.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-4.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-4.RAT | AI | Return air temp | 4-20mA | °C
AC-4.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-4.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-4.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-5.RUN | BI | Supply fan run status | DI dry contact | -
AC-5.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-5.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-5.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-5.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-5.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-5.RAT | AI | Return air temp | 4-20mA | °C
AC-5.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-5.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-5.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-5.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-5.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-6.RUN | BI | Supply fan run status | DI dry contact | -
AC-6.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-6.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-6.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-6.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-6.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-6.RAT | AI | Return air temp | 4-20mA | °C
AC-6.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-6.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-6.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-6.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-6.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-HSL-10
Control logic — DDC-HSL-10
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: AC-26
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling unit AC-26: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-26.RUN | BI | Supply fan run status | DI dry contact | -
AC-26.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-26.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-26.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-26.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-26.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-26.RAT | AI | Return air temp | 4-20mA | °C
AC-26.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-26.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-26.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-26.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-26.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-HSL-11
Control logic — DDC-HSL-11
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: FCU-L-N, FCU-L-NE, FCU-L-SE
Strategy: Zone thermostat + schedule batch
Sequence of Operations
Purpose
• Fan-coil zone group: maintain space temperature.
Control
• Zone thermostat cycles fan / modulates the coil valve; batch on/off and night-setback by the schedule; status/alarm to BMS.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FCU-L-N.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-L-N.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-L-N.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-L-N.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-L-N.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-L-N.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-L-N.RT | AI | Zone reference/return temp | 4-20mA | °C | Y
FCU-L-NE.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-L-NE.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-L-NE.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-L-NE.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-L-NE.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-L-NE.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-L-NE.RT | AI | Zone reference/return temp | 4-20mA | °C | Y
FCU-L-SE.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-L-SE.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-L-SE.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-L-SE.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-L-SE.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-L-SE.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-L-SE.RT | AI | Zone reference/return temp | 4-20mA | °C | Y

## DDC-HSL-12
Control logic — DDC-HSL-12
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: FCU-L-S, FCU-L-SW
Strategy: Zone thermostat + schedule batch
Sequence of Operations
Purpose
• Fan-coil zone group: maintain space temperature.
Control
• Zone thermostat cycles fan / modulates the coil valve; batch on/off and night-setback by the schedule; status/alarm to BMS.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FCU-L-S.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-L-S.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-L-S.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-L-S.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-L-S.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-L-S.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-L-S.RT | AI | Zone reference/return temp | 4-20mA | °C | Y
FCU-L-SW.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-L-SW.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-L-SW.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-L-SW.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-L-SW.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-L-SW.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-L-SW.RT | AI | Zone reference/return temp | 4-20mA | °C | Y

## DDC-HSL-13
Control logic — DDC-HSL-13
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: SF-6, EF-28, EF-32
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SF-6.SS | BO | Start/Stop command | DO relay | - | Y
SF-6.RUN | BI | Run status | DI dry contact | -
SF-6.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-28.SS | BO | Start/Stop command | DO relay | - | Y
EF-28.RUN | BI | Run status | DI dry contact | -
EF-28.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-32.SS | BO | Start/Stop command | DO relay | - | Y
EF-32.RUN | BI | Run status | DI dry contact | -
EF-32.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-HSL-14
Control logic — DDC-HSL-14
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: EF-33, EF-97, RF-7
Strategy: Scheduled ventilation / exhaust; Start/stop + status/alarm
Sequence of Operations
[Ventilation / exhaust fan] — EF-33, EF-97
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
[Field device] — RF-7
Purpose
• Supervise RF-7: start/stop, status and alarm as available.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-33.SS | BO | Start/Stop command | DO relay | - | Y
EF-33.RUN | BI | Run status | DI dry contact | -
EF-33.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-97.SS | BO | Start/Stop command | DO relay | - | Y
EF-97.RUN | BI | Run status | DI dry contact | -
EF-97.TRIP | BI | Fault | DI dry contact | - |  | Y
RF-7.SS | BO | Start/Stop command | DO relay | - | Y
RF-7.RUN | BI | Run status | DI dry contact | -
RF-7.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-HSL-15
Control logic — DDC-HSL-15
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: RF-8, RF-9
Strategy: Start/stop + status/alarm
Sequence of Operations
Purpose
• Supervise RF-8, RF-9: start/stop, status and alarm as available.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
RF-8.SS | BO | Start/Stop command | DO relay | - | Y
RF-8.RUN | BI | Run status | DI dry contact | -
RF-8.TRIP | BI | Fault | DI dry contact | - |  | Y
RF-9.SS | BO | Start/Stop command | DO relay | - | Y
RF-9.RUN | BI | Run status | DI dry contact | -
RF-9.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-HSL-16
Control logic — DDC-HSL-16
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: POOL-FP
Strategy: Start/stop + status/alarm
Sequence of Operations
Purpose
• Supervise POOL-FP: start/stop, status and alarm as available.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
POOL-FP.SS | BO | Start/Stop command | DO relay | - | Y
POOL-FP.RUN | BI | Run status | DI dry contact | -
POOL-FP.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-HSL-17
Control logic — DDC-HSL-17
Panel LCP-HSL (Low-rise distribution panel (低層系統)) · B2F Machine Room
Equipment: MTR-AHU-KWH
Strategy: Energy integration (monitor only)
Sequence of Operations
Purpose
• Energy metering (no control output).
Function
• Integrate pulse/analog energy for trend, demand limiting and peak monitoring; feed the dispatch/peak-shave logic.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
MTR-AHU-KWH | AI | AHU/OAU fans sub-meter | Pulse/Modbus | kWh

## DDC-HSH-01
Control logic — DDC-HSH-01
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: EX-3-1, EX-3-2
Strategy: Primary valve modulates to secondary outlet setpoint
Sequence of Operations
Purpose
• Transfer heat to the tempered loop; hold the secondary supply temperature.
Control
• Modulate primary control valve `*.PV` (feedback `*.PVFB`) to hold the secondary outlet setpoint `*.S-OUT` from primary inlet `*.P-IN`.
• Lead/lag/standby across 2 exchangers (EX-3-1, EX-3-2): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Safeties
• Freeze / high-temp limit on the secondary; valve-fault supervision; isolate on served-loop shutdown.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EX-3-1.P-IN | AI | Primary inlet temp (kitchen) | 4-20mA | °C
EX-3-1.S-OUT | AI | Secondary outlet (supply) temp | 4-20mA | °C | Y | Y
EX-3-1.PV | AO | Primary control valve | 0-10V | % | Y
EX-3-1.PVFB | AI | Primary valve position fb | 4-20mA | %
EX-3-2.P-IN | AI | Primary inlet temp (kitchen) | 4-20mA | °C
EX-3-2.S-OUT | AI | Secondary outlet (supply) temp | 4-20mA | °C | Y | Y
EX-3-2.PV | AO | Primary control valve | 0-10V | % | Y
EX-3-2.PVFB | AI | Primary valve position fb | 4-20mA | %

## DDC-HSH-02
Control logic — DDC-HSH-02
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: CP-2-1, CP-2-2, CP-2-3
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-2-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CP-2-1, CP-2-2, CP-2-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-2-1.RUN | BI | Run status | DI dry contact | -
CP-2-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-2-1.SS | BO | Start/Stop command | DO relay | -
CP-2-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-2-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-2-1.KW | AI | Power | 4-20mA | kW
CP-2-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-2-2.RUN | BI | Run status | DI dry contact | -
CP-2-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-2-2.SS | BO | Start/Stop command | DO relay | -
CP-2-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-2-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-2-2.KW | AI | Power | 4-20mA | kW
CP-2-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-2-3.RUN | BI | Run status | DI dry contact | -
CP-2-3.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-2-3.SS | BO | Start/Stop command | DO relay | -
CP-2-3.SPD | AO | VFD speed command | 0-10V | % | Y
CP-2-3.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-2-3.KW | AI | Power | 4-20mA | kW
CP-2-3.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSH-03
Control logic — DDC-HSH-03
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: CP-3-1, CP-3-2, CP-6-1
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-3-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CP-3-1, CP-3-2, CP-6-1): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-3-1.RUN | BI | Run status | DI dry contact | -
CP-3-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-3-1.SS | BO | Start/Stop command | DO relay | -
CP-3-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-3-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-3-1.KW | AI | Power | 4-20mA | kW
CP-3-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-3-2.RUN | BI | Run status | DI dry contact | -
CP-3-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-3-2.SS | BO | Start/Stop command | DO relay | -
CP-3-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-3-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-3-2.KW | AI | Power | 4-20mA | kW
CP-3-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-6-1.RUN | BI | Run status | DI dry contact | -
CP-6-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-6-1.SS | BO | Start/Stop command | DO relay | -
CP-6-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-6-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-6-1.KW | AI | Power | 4-20mA | kW
CP-6-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSH-04
Control logic — DDC-HSH-04
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: CP-6-2
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-6-2.SS`.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-6-2.RUN | BI | Run status | DI dry contact | -
CP-6-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-6-2.SS | BO | Start/Stop command | DO relay | -
CP-6-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-6-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-6-2.KW | AI | Power | 4-20mA | kW
CP-6-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSH-05
Control logic — DDC-HSH-05
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: HP-2-1, HP-2-2, HP-2-3
Strategy: Heating-season lead/lag to header Δp
Sequence of Operations
Purpose
• Hot-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `HP-2-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (HP-2-1, HP-2-2, HP-2-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HP-2-1.RUN | BI | Run status | DI dry contact | -
HP-2-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-2-1.SS | BO | Start/Stop command | DO relay | -
HP-2-1.SPD | AO | VFD speed command | 0-10V | % | Y
HP-2-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-2-1.KW | AI | Power | 4-20mA | kW
HP-2-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-2-2.RUN | BI | Run status | DI dry contact | -
HP-2-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-2-2.SS | BO | Start/Stop command | DO relay | -
HP-2-2.SPD | AO | VFD speed command | 0-10V | % | Y
HP-2-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-2-2.KW | AI | Power | 4-20mA | kW
HP-2-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-2-3.RUN | BI | Run status | DI dry contact | -
HP-2-3.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-2-3.SS | BO | Start/Stop command | DO relay | -
HP-2-3.SPD | AO | VFD speed command | 0-10V | % | Y
HP-2-3.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-2-3.KW | AI | Power | 4-20mA | kW
HP-2-3.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-HSH-06
Control logic — DDC-HSH-06
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: EXT-2
Strategy: Loop pressurisation
Sequence of Operations
Purpose
• Loop pressurisation / expansion set.
Control
• Maintain fill pressure via makeup valve/pump; low-pressure & level alarms.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EXT-2.LVL | AI | Tank level | 4-20mA | % |  | Y
EXT-2.HI | BI | High-level alarm | DI dry contact | - |  | Y
EXT-2.LO | BI | Low-level alarm | DI dry contact | - |  | Y

## DDC-HSH-07
Control logic — DDC-HSH-07
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: ST-2
Strategy: OA tempering to setpoint
Sequence of Operations
Purpose
• Outdoor-air station: temper and deliver ventilation air to the loop.
Control
• Modulate to the OA supply setpoint; enable with the served distribution; economizer-favourable in shoulder season.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
ST-2.T | AI | Outdoor dry-bulb temp | 4-20mA | °C
ST-2.RH | AI | Outdoor humidity | 4-20mA | %RH
ST-2.WB | AI | Wet-bulb temp (計測/演算) | 4-20mA | °C

## DDC-HSH-08
Control logic — DDC-HSH-08
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: EVU-11, EVU-12, EVU-13
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EVU-11.RUN | BI | Supply fan run status | DI dry contact | -
EVU-11.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-11.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-11.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
EVU-11.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
EVU-11.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-11.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-11.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-11.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-11.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-11.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-11.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-11.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-12.RUN | BI | Supply fan run status | DI dry contact | -
EVU-12.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-12.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-12.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
EVU-12.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
EVU-12.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-12.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-12.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-12.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-12.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-12.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-12.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-12.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-13.RUN | BI | Supply fan run status | DI dry contact | -
EVU-13.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-13.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-13.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
EVU-13.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
EVU-13.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-13.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-13.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-13.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-13.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-13.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-13.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-13.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-HSH-09
Control logic — DDC-HSH-09
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: EVU-14, EVU-15
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EVU-14.RUN | BI | Supply fan run status | DI dry contact | -
EVU-14.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-14.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-14.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-14.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-14.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-14.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-14.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-14.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-14.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-14.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-14.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-15.RUN | BI | Supply fan run status | DI dry contact | -
EVU-15.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-15.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-15.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-15.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-15.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-15.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-15.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-15.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-15.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-15.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-15.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-HSH-10
Control logic — DDC-HSH-10
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: FCU-H-N, FCU-H-NE, FCU-H-SE
Strategy: Zone thermostat + schedule batch
Sequence of Operations
Purpose
• Fan-coil zone group: maintain space temperature.
Control
• Zone thermostat cycles fan / modulates the coil valve; batch on/off and night-setback by the schedule; status/alarm to BMS.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FCU-H-N.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-H-N.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-H-N.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-H-N.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-H-N.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-H-N.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-H-N.RT | AI | Zone reference/return temp | 4-20mA | °C | Y
FCU-H-NE.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-H-NE.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-H-NE.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-H-NE.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-H-NE.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-H-NE.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-H-NE.RT | AI | Zone reference/return temp | 4-20mA | °C | Y
FCU-H-SE.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-H-SE.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-H-SE.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-H-SE.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-H-SE.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-H-SE.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-H-SE.RT | AI | Zone reference/return temp | 4-20mA | °C | Y

## DDC-HSH-11
Control logic — DDC-HSH-11
Panel LCP-HSH (High-rise distribution panel (高層系統)) · PH Machine Room
Equipment: FCU-H-S, FCU-H-SW
Strategy: Zone thermostat + schedule batch
Sequence of Operations
Purpose
• Fan-coil zone group: maintain space temperature.
Control
• Zone thermostat cycles fan / modulates the coil valve; batch on/off and night-setback by the schedule; status/alarm to BMS.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FCU-H-S.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-H-S.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-H-S.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-H-S.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-H-S.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-H-S.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-H-S.RT | AI | Zone reference/return temp | 4-20mA | °C | Y
FCU-H-SW.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-H-SW.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-H-SW.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-H-SW.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-H-SW.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-H-SW.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-H-SW.RT | AI | Zone reference/return temp | 4-20mA | °C | Y

## DDC-3637-01
Control logic — DDC-3637-01
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: R-1
Strategy: Economic dispatch + CHW/CW reset + twin-screw staging
Sequence of Operations
Purpose
• R-1 is the local water-cooled twin-screw chiller (Ebara RHS DW202M2, 370 kW, COP 4.5) that backs up / peak-shaves the DHC supply on the 36/37F loop.
Economic dispatch (DHC vs R-1)
• DHC is the default source. Stage the chiller only when its marginal cost beats DHC by >5% or DHC is unavailable: run when `DHC_cost > R-1_cost x 1.05` and loop PLR > 0.15.
• Enable via `R-1.SS`; trim capacity with `R-1.DMD`. During the DHC coincident-peak window the demand adder pushes DHC above R-1 -> peak-shave mode.
• Bumpless changeover through CHGV-1/2 (branch vs through-main); no compressor start without both evaporator and condenser flow proven.
Capacity, staging & resets
• Twin 45 kW screws: one up to ~55% loop PLR, both above; balanced load-share; anti-short-cycle min-on/off; rotate lead daily.
• CHW reset (trim-and-respond) 7->10 C to most-open coil; hold via `R-1.CHWST` (return `R-1.CHWRT`). Condenser-water reset = wet-bulb + 3.5 C, floored at 19 C (R-407C min-lift), tracked on `R-1.CWRT` via CT-3/CDP-3.
Safeties, backup & monitoring
• Flow-proof + freeze + hi-discharge/low-suction interlocks; trip on `R-1.TRIP`; honour `R-1.LR` (local/remote).
• Weekly readiness exercise (Mon 10:00) when otherwise idle; live COP / kW-per-RT and evap/cond approach for FDD (low-DT, condenser fouling).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
R-1.RUN | BI | Run status | DI dry contact | -
R-1.TRIP | BI | Common fault / trip | DI dry contact | - |  | Y
R-1.LR | BI | Local/Remote status | DI dry contact | -
R-1.SS | BO | Start/Stop command | DO relay | - | Y
R-1.DMD | AO | Capacity/demand limit | 0-10V | % | Y
R-1.CHWST | AI | CHW supply (leaving) temp | 4-20mA | °C |  | Y
R-1.CHWRT | AI | CHW return (entering) temp | 4-20mA | °C
R-1.CWRT | AI | Condenser water leaving temp | 4-20mA | °C
R-1.KW | AI | Electrical input power | 4-20mA | kW
R-1.FLW | BI | Evaporator flow proof | DI dry contact | - |  | Y

## DDC-3637-02
Control logic — DDC-3637-02
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: HEX-1
Strategy: Primary valve modulates to secondary outlet setpoint
Sequence of Operations
Purpose
• Transfer heat to the tempered loop; hold the secondary supply temperature.
Control
• Modulate primary control valve `*.PV` (feedback `*.PVFB`) to hold the secondary outlet setpoint `*.S-OUT` from primary inlet `*.P-IN`.
Safeties
• Freeze / high-temp limit on the secondary; valve-fault supervision; isolate on served-loop shutdown.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HEX-1.P-IN | AI | Primary (DHC) inlet temp | 4-20mA | °C
HEX-1.P-OUT | AI | Primary (DHC) outlet temp | 4-20mA | °C
HEX-1.S-OUT | AI | Secondary (loop) supply temp | 4-20mA | °C | Y | Y
HEX-1.S-FLW | AI | Secondary supply flow | 4-20mA | m³/h
HEX-1.GJ | AI | DHC thermal-energy meter | Pulse/Modbus | MJ
HEX-1.PV | AO | Primary control valve | 0-10V | % | Y
HEX-1.PVFB | AI | Primary valve position fb | 4-20mA | %

## DDC-3637-03
Control logic — DDC-3637-03
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: CP-7-1, CP-7-2, CP-8-1
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-7-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 3 pumps (CP-7-1, CP-7-2, CP-8-1): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-7-1.RUN | BI | Run status | DI dry contact | -
CP-7-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-7-1.SS | BO | Start/Stop command | DO relay | -
CP-7-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-7-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-7-1.KW | AI | Power | 4-20mA | kW
CP-7-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-7-2.RUN | BI | Run status | DI dry contact | -
CP-7-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-7-2.SS | BO | Start/Stop command | DO relay | -
CP-7-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-7-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-7-2.KW | AI | Power | 4-20mA | kW
CP-7-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-8-1.RUN | BI | Run status | DI dry contact | -
CP-8-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-8-1.SS | BO | Start/Stop command | DO relay | -
CP-8-1.SPD | AO | VFD speed command | 0-10V | % | Y
CP-8-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-8-1.KW | AI | Power | 4-20mA | kW
CP-8-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-3637-04
Control logic — DDC-3637-04
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: CP-8-2, CP-8-3
Strategy: Lead/lag VFD to header Δp (variable flow)
Sequence of Operations
Purpose
• Chilled-water distribution pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `CP-8-2.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 2 pumps (CP-8-2, CP-8-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CP-8-2.RUN | BI | Run status | DI dry contact | -
CP-8-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-8-2.SS | BO | Start/Stop command | DO relay | -
CP-8-2.SPD | AO | VFD speed command | 0-10V | % | Y
CP-8-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-8-2.KW | AI | Power | 4-20mA | kW
CP-8-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
CP-8-3.RUN | BI | Run status | DI dry contact | -
CP-8-3.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
CP-8-3.SS | BO | Start/Stop command | DO relay | -
CP-8-3.SPD | AO | VFD speed command | 0-10V | % | Y
CP-8-3.SPDFB | AI | VFD speed feedback | 4-20mA | %
CP-8-3.KW | AI | Power | 4-20mA | kW
CP-8-3.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-3637-05
Control logic — DDC-3637-05
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: HP-4-1, HP-4-2
Strategy: Buffer-loop lead/lag to Δp
Sequence of Operations
Purpose
• Secondary buffer-loop pumps: maintain loop flow for the served load.
Sequencing
• Start/stop on system demand via `HP-4-1.SS`, one pump at a time with flow/Δp proof.
• Lead/lag/standby across 2 pumps (HP-4-1, HP-4-2): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Modulation & reset
• VFD (`*.SPD`, feedback `*.SPDFB`) modulates to hold the header differential pressure; reset the Δp setpoint down to the most-open served valve (variable-flow).
Safeties & monitoring
• Prove flow before loading; trip on `*.TRIP`; low-Δp / no-flow and pump-fault alarms; protect duty OR standby availability at all times.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
HP-4-1.RUN | BI | Run status | DI dry contact | -
HP-4-1.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-4-1.SS | BO | Start/Stop command | DO relay | -
HP-4-1.SPD | AO | VFD speed command | 0-10V | % | Y
HP-4-1.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-4-1.KW | AI | Power | 4-20mA | kW
HP-4-1.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y
HP-4-2.RUN | BI | Run status | DI dry contact | -
HP-4-2.TRIP | BI | VFD/pump fault | DI dry contact | - |  | Y
HP-4-2.SS | BO | Start/Stop command | DO relay | -
HP-4-2.SPD | AO | VFD speed command | 0-10V | % | Y
HP-4-2.SPDFB | AI | VFD speed feedback | 4-20mA | %
HP-4-2.KW | AI | Power | 4-20mA | kW
HP-4-2.FLW | BI | Flow/DP proof | DI dry contact | - |  | Y

## DDC-3637-06
Control logic — DDC-3637-06
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: EX4, EXT-3
Strategy: Primary valve modulates to secondary outlet setpoint; Loop pressurisation
Sequence of Operations
[Plate heat exchanger (heating/tempered loop)] — EX4
Purpose
• Transfer heat to the tempered loop; hold the secondary supply temperature.
Control
• Modulate primary control valve `*.PV` (feedback `*.PVFB`) to hold the secondary outlet setpoint `*.S-OUT` from primary inlet `*.P-IN`.
Safeties
• Freeze / high-temp limit on the secondary; valve-fault supervision; isolate on served-loop shutdown.
[Expansion / pressurisation set] — EXT-3
Purpose
• Loop pressurisation / expansion set.
Control
• Maintain fill pressure via makeup valve/pump; low-pressure & level alarms.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EX4.P-IN | AI | Primary inlet temp (36/37F loop) | 4-20mA | °C
EX4.S-OUT | AI | Secondary outlet (supply) temp | 4-20mA | °C | Y | Y
EX4.PV | AO | Primary control valve | 0-10V | % | Y
EX4.PVFB | AI | Primary valve position fb | 4-20mA | %
EXT-3.LVL | AI | Tank level | 4-20mA | % |  | Y
EXT-3.HI | BI | High-level alarm | DI dry contact | - |  | Y
EXT-3.LO | BI | Low-level alarm | DI dry contact | - |  | Y

## DDC-3637-07
Control logic — DDC-3637-07
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: CHGV-1, CHGV-2
Strategy: Bumpless source transfer + flow proof
Sequence of Operations
Purpose
• Source-changeover valve set (R-1 branch vs DHC through-main).
Control
• Sequenced bumpless transfer with flow proof before compressor enable; position feedback and end-switch supervision.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
CHGV-1.CMD | BO | Open/close command | DO relay | - | Y
CHGV-1.ST | BI | Position status | DI dry contact | - |  | Y
CHGV-2.CMD | BO | Open/close command | DO relay | - | Y
CHGV-2.ST | BI | Position status | DI dry contact | - |  | Y

## DDC-3637-08
Control logic — DDC-3637-08
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: AC-22, AC-23, AC-24
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-22, AC-23, AC-24: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-22.RUN | BI | Supply fan run status | DI dry contact | -
AC-22.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-22.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-22.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-22.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-22.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-22.RAT | AI | Return air temp | 4-20mA | °C
AC-22.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-22.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-22.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-22.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-22.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-23.RUN | BI | Supply fan run status | DI dry contact | -
AC-23.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-23.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-23.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-23.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-23.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-23.RAT | AI | Return air temp | 4-20mA | °C
AC-23.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-23.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-23.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-23.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-23.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-24.RUN | BI | Supply fan run status | DI dry contact | -
AC-24.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-24.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-24.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-24.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-24.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-24.RAT | AI | Return air temp | 4-20mA | °C
AC-24.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-24.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-24.HUM | AO | Steam humidifier valve | 0-10V | % | Y
AC-24.RH | AI | Return/space humidity | 4-20mA | %RH
AC-24.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-24.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-24.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-3637-09
Control logic — DDC-3637-09
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: AC-25, AC-27
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-25, AC-27: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-25.RUN | BI | Supply fan run status | DI dry contact | -
AC-25.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-25.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-25.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-25.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-25.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-25.RAT | AI | Return air temp | 4-20mA | °C
AC-25.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-25.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-25.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-25.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-25.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-27.RUN | BI | Supply fan run status | DI dry contact | -
AC-27.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-27.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-27.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-27.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-27.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-27.RAT | AI | Return air temp | 4-20mA | °C
AC-27.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-27.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-27.HUM | AO | Steam humidifier valve | 0-10V | % | Y
AC-27.RH | AI | Return/space humidity | 4-20mA | %RH
AC-27.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-27.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-27.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-3637-10
Control logic — DDC-3637-10
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: FCU-3637
Strategy: Zone thermostat + schedule batch
Sequence of Operations
Purpose
• Fan-coil zone group: maintain space temperature.
Control
• Zone thermostat cycles fan / modulates the coil valve; batch on/off and night-setback by the schedule; status/alarm to BMS.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FCU-3637.EN | BO | Group enable / schedule | DO relay | - | Y
FCU-3637.MODE | BI | Cooling/Heating changeover status | DI dry contact | -
FCU-3637.CWV | AO | Chilled-water group valve | 0-10V | % | Y
FCU-3637.HWV | AO | Hot-water group valve | 0-10V | % | Y
FCU-3637.CWBV-F | BI | Chilled-water BV batch fault | DI dry contact | - |  | Y
FCU-3637.HWBV-F | BI | Hot-water BV batch fault | DI dry contact | - |  | Y
FCU-3637.RT | AI | Zone reference/return temp | 4-20mA | °C | Y

## DDC-3637-11
Control logic — DDC-3637-11
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: EF-82, EF-83, EF-84
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-82.SS | BO | Start/Stop command | DO relay | - | Y
EF-82.RUN | BI | Run status | DI dry contact | -
EF-82.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-83.SS | BO | Start/Stop command | DO relay | - | Y
EF-83.RUN | BI | Run status | DI dry contact | -
EF-83.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-83.SPD | AO | VFD (INV) speed command | 0-10V | % | Y
EF-83.SPDFB | AI | VFD speed feedback | 4-20mA | %
EF-84.SS | BO | Start/Stop command | DO relay | - | Y
EF-84.RUN | BI | Run status | DI dry contact | -
EF-84.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-3637-12
Control logic — DDC-3637-12
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: EF-85, EF-86, EF-89
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-85.SS | BO | Start/Stop command | DO relay | - | Y
EF-85.RUN | BI | Run status | DI dry contact | -
EF-85.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-86.SS | BO | Start/Stop command | DO relay | - | Y
EF-86.RUN | BI | Run status | DI dry contact | -
EF-86.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-89.SS | BO | Start/Stop command | DO relay | - | Y
EF-89.RUN | BI | Run status | DI dry contact | -
EF-89.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-3637-13
Control logic — DDC-3637-13
Panel LCP-3637 (36/37F local heat-source panel (36,37F系統)) · 37F PH Machine Room
Equipment: EF-98
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-98.SS | BO | Start/Stop command | DO relay | - | Y
EF-98.RUN | BI | Run status | DI dry contact | -
EF-98.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-1F-01
Control logic — DDC-1F-01
Panel LCP-1F (1F–2F air-side panel) · 1F EPS/AHU Room
Equipment: AC-7
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling unit AC-7: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-7.RUN | BI | Supply fan run status | DI dry contact | -
AC-7.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-7.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-7.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-7.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-7.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-7.RAT | AI | Return air temp | 4-20mA | °C
AC-7.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-7.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-7.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-7.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-7.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-1F-02
Control logic — DDC-1F-02
Panel LCP-1F (1F–2F air-side panel) · 1F EPS/AHU Room
Equipment: EVU-1, EVU-2, EVU-3
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EVU-1.RUN | BI | Supply fan run status | DI dry contact | -
EVU-1.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-1.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-1.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-1.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-1.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-1.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-1.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-1.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-1.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-1.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-1.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-2.RUN | BI | Supply fan run status | DI dry contact | -
EVU-2.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-2.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-2.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-2.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-2.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-2.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-2.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-2.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-2.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-2.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-2.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-3.RUN | BI | Supply fan run status | DI dry contact | -
EVU-3.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-3.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-3.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-3.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-3.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-3.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-3.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-3.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-3.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-3.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-3.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-1F-03
Control logic — DDC-1F-03
Panel LCP-1F (1F–2F air-side panel) · 1F EPS/AHU Room
Equipment: EF-41, EF-42
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-41.SS | BO | Start/Stop command | DO relay | - | Y
EF-41.RUN | BI | Run status | DI dry contact | -
EF-41.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-42.SS | BO | Start/Stop command | DO relay | - | Y
EF-42.RUN | BI | Run status | DI dry contact | -
EF-42.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-2F-01
Control logic — DDC-2F-01
Panel LCP-2F (2F air-side panel) · 2F AHU Room
Equipment: AC-8, AC-9, AC-10
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-8, AC-9, AC-10: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-8.RUN | BI | Supply fan run status | DI dry contact | -
AC-8.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-8.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-8.SPD | AO | Supply fan speed (fixed) | 0-10V | %
AC-8.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-8.RAT | AI | Return air temp | 4-20mA | °C
AC-8.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-8.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-8.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-8.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-8.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-9.RUN | BI | Supply fan run status | DI dry contact | -
AC-9.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-9.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-9.SPD | AO | Supply fan speed (fixed) | 0-10V | %
AC-9.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-9.RAT | AI | Return air temp | 4-20mA | °C
AC-9.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-9.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-9.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-9.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-9.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-10.RUN | BI | Supply fan run status | DI dry contact | -
AC-10.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-10.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-10.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-10.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-10.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-10.RAT | AI | Return air temp | 4-20mA | °C
AC-10.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-10.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-10.HUM | AO | Steam humidifier valve | 0-10V | % | Y
AC-10.RH | AI | Return/space humidity | 4-20mA | %RH
AC-10.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-10.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-10.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-2F-02
Control logic — DDC-2F-02
Panel LCP-2F (2F air-side panel) · 2F AHU Room
Equipment: AC-11, AC-12, AC-13
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-11, AC-12, AC-13: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-11.RUN | BI | Supply fan run status | DI dry contact | -
AC-11.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-11.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-11.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-11.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-11.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-11.RAT | AI | Return air temp | 4-20mA | °C
AC-11.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-11.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-11.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-11.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-11.CO2 | AI | Space CO2 concentration | 4-20mA | ppm | Y | Y
AC-11.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-12.RUN | BI | Supply fan run status | DI dry contact | -
AC-12.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-12.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-12.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-12.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-12.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-12.RAT | AI | Return air temp | 4-20mA | °C
AC-12.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-12.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-12.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-12.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-12.CO2 | AI | Space CO2 concentration | 4-20mA | ppm | Y | Y
AC-12.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-13.RUN | BI | Supply fan run status | DI dry contact | -
AC-13.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-13.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-13.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-13.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-13.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-13.RAT | AI | Return air temp | 4-20mA | °C
AC-13.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-13.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-13.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-13.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-13.CO2 | AI | Space CO2 concentration | 4-20mA | ppm | Y | Y
AC-13.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-2F-03
Control logic — DDC-2F-03
Panel LCP-2F (2F air-side panel) · 2F AHU Room
Equipment: EVU-4, EVU-5, EVU-6
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EVU-4.RUN | BI | Supply fan run status | DI dry contact | -
EVU-4.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-4.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-4.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-4.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-4.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-4.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-4.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-4.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-4.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-4.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-4.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-5.RUN | BI | Supply fan run status | DI dry contact | -
EVU-5.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-5.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-5.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-5.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-5.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-5.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-5.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-5.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-5.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-5.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-5.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-6.RUN | BI | Supply fan run status | DI dry contact | -
EVU-6.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-6.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-6.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-6.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-6.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-6.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-6.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-6.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-6.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-6.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-6.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-2F-04
Control logic — DDC-2F-04
Panel LCP-2F (2F air-side panel) · 2F AHU Room
Equipment: EF-2-1, EF-46, EF-47
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-2-1.SS | BO | Start/Stop command | DO relay | - | Y
EF-2-1.RUN | BI | Run status | DI dry contact | -
EF-2-1.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-46.SS | BO | Start/Stop command | DO relay | - | Y
EF-46.RUN | BI | Run status | DI dry contact | -
EF-46.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-47.SS | BO | Start/Stop command | DO relay | - | Y
EF-47.RUN | BI | Run status | DI dry contact | -
EF-47.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-3F-01
Control logic — DDC-3F-01
Panel LCP-3F (3F air-side panel) · 3F AHU Room
Equipment: AC-14, AC-15, AC-16
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-14, AC-15, AC-16: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-14.RUN | BI | Supply fan run status | DI dry contact | -
AC-14.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-14.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-14.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-14.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-14.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-14.RAT | AI | Return air temp | 4-20mA | °C
AC-14.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-14.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-14.HUM | AO | Steam humidifier valve | 0-10V | % | Y
AC-14.RH | AI | Return/space humidity | 4-20mA | %RH
AC-14.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-14.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-14.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-15.RUN | BI | Supply fan run status | DI dry contact | -
AC-15.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-15.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-15.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-15.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-15.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-15.RAT | AI | Return air temp | 4-20mA | °C
AC-15.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-15.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-15.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-15.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-15.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-16.RUN | BI | Supply fan run status | DI dry contact | -
AC-16.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-16.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-16.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-16.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-16.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-16.RAT | AI | Return air temp | 4-20mA | °C
AC-16.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-16.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-16.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-16.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-16.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-3F-02
Control logic — DDC-3F-02
Panel LCP-3F (3F air-side panel) · 3F AHU Room
Equipment: EVU-7
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EVU-7.RUN | BI | Supply fan run status | DI dry contact | -
EVU-7.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-7.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-7.SPD | AO | Supply fan speed (fixed) | 0-10V | %
EVU-7.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-7.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-7.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-7.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-7.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-7.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-7.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-7.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-3F-03
Control logic — DDC-3F-03
Panel LCP-3F (3F air-side panel) · 3F AHU Room
Equipment: EF-56, EF-60, EF-61
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-56.SS | BO | Start/Stop command | DO relay | - | Y
EF-56.RUN | BI | Run status | DI dry contact | -
EF-56.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-60.SS | BO | Start/Stop command | DO relay | - | Y
EF-60.RUN | BI | Run status | DI dry contact | -
EF-60.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-61.SS | BO | Start/Stop command | DO relay | - | Y
EF-61.RUN | BI | Run status | DI dry contact | -
EF-61.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-3F-04
Control logic — DDC-3F-04
Panel LCP-3F (3F air-side panel) · 3F AHU Room
Equipment: EF-62, EF-76, EF-77
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-62.SS | BO | Start/Stop command | DO relay | - | Y
EF-62.RUN | BI | Run status | DI dry contact | -
EF-62.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-76.SS | BO | Start/Stop command | DO relay | - | Y
EF-76.RUN | BI | Run status | DI dry contact | -
EF-76.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-77.SS | BO | Start/Stop command | DO relay | - | Y
EF-77.RUN | BI | Run status | DI dry contact | -
EF-77.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-4F-01
Control logic — DDC-4F-01
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: AC-17, AC-18, AC-19
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-17, AC-18, AC-19: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-17.RUN | BI | Supply fan run status | DI dry contact | -
AC-17.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-17.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-17.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-17.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-17.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-17.RAT | AI | Return air temp | 4-20mA | °C
AC-17.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-17.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-17.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-17.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-17.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-18.RUN | BI | Supply fan run status | DI dry contact | -
AC-18.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-18.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-18.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-18.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-18.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-18.RAT | AI | Return air temp | 4-20mA | °C
AC-18.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-18.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-18.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-18.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-18.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-19.RUN | BI | Supply fan run status | DI dry contact | -
AC-19.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-19.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-19.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-19.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-19.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-19.RAT | AI | Return air temp | 4-20mA | °C
AC-19.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-19.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-19.HUM | AO | Steam humidifier valve | 0-10V | % | Y
AC-19.RH | AI | Return/space humidity | 4-20mA | %RH
AC-19.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-19.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-19.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-4F-02
Control logic — DDC-4F-02
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: AC-20, AC-21
Strategy: Schedule + SAT coil control + economizer
Sequence of Operations
Purpose
• Air-handling units AC-20, AC-21: maintain supply-air temperature and space conditions on the occupancy schedule.
Start / fan control
• Start/stop `*.SS` on the occupancy time-program; prove `*.RUN`, alarm `*.TRIP`.
• VFD supply fan `*.SPD` (feedback `*.SPDFB`) to duct static / demand.
Temperature control
• Cooling coil `*.CCV` modulates to hold supply-air temp `*.SAT` (return `*.RAT`).
• Heating coil `*.HCV` sequenced with a deadband (no simultaneous heat/cool).
• Shoulder-season (Apr–May): drive to OA economizer / free-cooling — 100% OA, cooling coil closed — per the cutover plan.
Safeties & monitoring
• Freeze-stat, fan-status proof, filter-DP and smoke/fire interlock (shut fan, spring-return dampers); high supply-temp alarm `*.SAT`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
AC-20.RUN | BI | Supply fan run status | DI dry contact | -
AC-20.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-20.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-20.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-20.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-20.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-20.RAT | AI | Return air temp | 4-20mA | °C
AC-20.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-20.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-20.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-20.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-20.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
AC-21.RUN | BI | Supply fan run status | DI dry contact | -
AC-21.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
AC-21.SS | BO | Supply fan start/stop | DO relay | - | Y
AC-21.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
AC-21.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
AC-21.SAT | AI | Supply air temp | 4-20mA | °C | Y | Y
AC-21.RAT | AI | Return air temp | 4-20mA | °C
AC-21.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
AC-21.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
AC-21.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
AC-21.OAD | AO | Outdoor-air damper | 0-10V | % | Y
AC-21.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-4F-03
Control logic — DDC-4F-03
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: EVU-8, EVU-9, EVU-10
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EVU-8.RUN | BI | Supply fan run status | DI dry contact | -
EVU-8.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-8.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-8.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
EVU-8.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
EVU-8.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-8.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-8.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-8.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-8.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-8.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-8.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-8.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-9.RUN | BI | Supply fan run status | DI dry contact | -
EVU-9.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-9.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-9.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
EVU-9.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
EVU-9.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-9.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-9.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-9.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-9.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-9.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-9.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-9.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y
EVU-10.RUN | BI | Supply fan run status | DI dry contact | -
EVU-10.TRIP | BI | Supply fan fault | DI dry contact | - |  | Y
EVU-10.SS | BO | Supply fan start/stop | DO relay | - | Y
EVU-10.SPD | AO | Supply fan VFD (INV) speed | 0-10V | % | Y
EVU-10.SPDFB | AI | Supply fan speed feedback | 4-20mA | %
EVU-10.SAT | AI | Supply (off-coil) air temp | 4-20mA | °C | Y | Y
EVU-10.OAT | AI | Outdoor-air temp (unit inlet) | 4-20mA | °C
EVU-10.OARH | AI | Outdoor-air humidity | 4-20mA | %RH
EVU-10.CCV | AO | Cooling coil (CHW) valve | 0-10V | % | Y
EVU-10.HCV | AO | Heating coil (steam) valve | 0-10V | % | Y
EVU-10.HUM | AO | Steam humidifier valve | 0-10V | % | Y
EVU-10.FLT | BI | Filter dirty (DP) | DI dry contact | - |  | Y
EVU-10.FRZ | BI | Freeze protection stat | DI dry contact | - |  | Y

## DDC-4F-04
Control logic — DDC-4F-04
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: EF-54, EF-55, EF-57
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-54.SS | BO | Start/Stop command | DO relay | - | Y
EF-54.RUN | BI | Run status | DI dry contact | -
EF-54.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-55.SS | BO | Start/Stop command | DO relay | - | Y
EF-55.RUN | BI | Run status | DI dry contact | -
EF-55.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-57.SS | BO | Start/Stop command | DO relay | - | Y
EF-57.RUN | BI | Run status | DI dry contact | -
EF-57.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-4F-05
Control logic — DDC-4F-05
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: EF-58, EF-59, EF-59-2
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-58.SS | BO | Start/Stop command | DO relay | - | Y
EF-58.RUN | BI | Run status | DI dry contact | -
EF-58.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-59.SS | BO | Start/Stop command | DO relay | - | Y
EF-59.RUN | BI | Run status | DI dry contact | -
EF-59.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-59-2.SS | BO | Start/Stop command | DO relay | - | Y
EF-59-2.RUN | BI | Run status | DI dry contact | -
EF-59-2.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-4F-06
Control logic — DDC-4F-06
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: EF-67, EF-69, EF-70
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-67.SS | BO | Start/Stop command | DO relay | - | Y
EF-67.RUN | BI | Run status | DI dry contact | -
EF-67.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-69.SS | BO | Start/Stop command | DO relay | - | Y
EF-69.RUN | BI | Run status | DI dry contact | -
EF-69.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-70.SS | BO | Start/Stop command | DO relay | - | Y
EF-70.RUN | BI | Run status | DI dry contact | -
EF-70.TRIP | BI | Fault | DI dry contact | - |  | Y
EF-70.SPD | AO | VFD (INV) speed command | 0-10V | % | Y
EF-70.SPDFB | AI | VFD speed feedback | 4-20mA | %

## DDC-4F-07
Control logic — DDC-4F-07
Panel LCP-4F (4F–5F air-side panel) · 4F AHU Room
Equipment: EF-71
Strategy: Scheduled ventilation / exhaust
Sequence of Operations
Purpose
• Ventilation / exhaust: run to the occupancy schedule and IAQ demand.
Control
• Start/stop `*.SS` on schedule; interlock with associated AHU / fire mode; prove `*.RUN`, alarm `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
EF-71.SS | BO | Start/Stop command | DO relay | - | Y
EF-71.RUN | BI | Run status | DI dry contact | -
EF-71.TRIP | BI | Fault | DI dry contact | - |  | Y

## DDC-PKG-01
Control logic — DDC-PKG-01
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: PAC-1-1, PAC-1-2, PAC-2
Strategy: Enable/monitor; integral DX (some 24/7)
Sequence of Operations
Purpose
• Packaged DX units (PAC-1-1, PAC-1-2, PAC-2) — several serve IT/electrical rooms and run continuously.
Control & monitoring
• BMS enables/schedules via `*.SS` and monitors run `*.RUN` + fault `*.TRIP`; capacity is on the unit's integral DX thermostat.
• Electrical/IT-room units are 24/7 — treat as critical (stage spare cooling before any swap).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
PAC-1-1.RUN | BI | Run status | DI dry contact | -
PAC-1-1.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PAC-1-1.SS | BO | Start/Stop command | DO relay | - | Y
PAC-1-2.RUN | BI | Run status | DI dry contact | -
PAC-1-2.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PAC-1-2.SS | BO | Start/Stop command | DO relay | - | Y
PAC-2.RUN | BI | Run status | DI dry contact | -
PAC-2.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PAC-2.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-PKG-02
Control logic — DDC-PKG-02
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: PAC-3, PAC-4, PAC-5
Strategy: Enable/monitor; integral DX (some 24/7)
Sequence of Operations
Purpose
• Packaged DX units (PAC-3, PAC-4, PAC-5) — several serve IT/electrical rooms and run continuously.
Control & monitoring
• BMS enables/schedules via `*.SS` and monitors run `*.RUN` + fault `*.TRIP`; capacity is on the unit's integral DX thermostat.
• Electrical/IT-room units are 24/7 — treat as critical (stage spare cooling before any swap).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
PAC-3.RUN | BI | Run status | DI dry contact | -
PAC-3.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PAC-3.SS | BO | Start/Stop command | DO relay | - | Y
PAC-4.RUN | BI | Run status | DI dry contact | -
PAC-4.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PAC-4.SS | BO | Start/Stop command | DO relay | - | Y
PAC-5.RUN | BI | Run status | DI dry contact | -
PAC-5.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PAC-5.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-PKG-03
Control logic — DDC-PKG-03
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: PCU-1-1, PCU-1-2, PCU-5
Strategy: Enable/monitor; integral DX (some 24/7)
Sequence of Operations
Purpose
• Packaged DX units (PCU-1-1, PCU-1-2, PCU-5) — several serve IT/electrical rooms and run continuously.
Control & monitoring
• BMS enables/schedules via `*.SS` and monitors run `*.RUN` + fault `*.TRIP`; capacity is on the unit's integral DX thermostat.
• Electrical/IT-room units are 24/7 — treat as critical (stage spare cooling before any swap).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
PCU-1-1.RUN | BI | Run status | DI dry contact | -
PCU-1-1.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-1-1.SS | BO | Start/Stop command | DO relay | - | Y
PCU-1-2.RUN | BI | Run status | DI dry contact | -
PCU-1-2.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-1-2.SS | BO | Start/Stop command | DO relay | - | Y
PCU-5.RUN | BI | Run status | DI dry contact | -
PCU-5.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-5.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-PKG-04
Control logic — DDC-PKG-04
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: PCU-6, PCU-7, PCU-8
Strategy: Enable/monitor; integral DX (some 24/7)
Sequence of Operations
Purpose
• Packaged DX units (PCU-6, PCU-7, PCU-8) — several serve IT/electrical rooms and run continuously.
Control & monitoring
• BMS enables/schedules via `*.SS` and monitors run `*.RUN` + fault `*.TRIP`; capacity is on the unit's integral DX thermostat.
• Electrical/IT-room units are 24/7 — treat as critical (stage spare cooling before any swap).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
PCU-6.RUN | BI | Run status | DI dry contact | -
PCU-6.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-6.SS | BO | Start/Stop command | DO relay | - | Y
PCU-7.RUN | BI | Run status | DI dry contact | -
PCU-7.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-7.SS | BO | Start/Stop command | DO relay | - | Y
PCU-8.RUN | BI | Run status | DI dry contact | -
PCU-8.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-8.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-PKG-05
Control logic — DDC-PKG-05
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: PCU-10, PCU-11, PCU-12
Strategy: Enable/monitor; integral DX (some 24/7)
Sequence of Operations
Purpose
• Packaged DX units (PCU-10, PCU-11, PCU-12) — several serve IT/electrical rooms and run continuously.
Control & monitoring
• BMS enables/schedules via `*.SS` and monitors run `*.RUN` + fault `*.TRIP`; capacity is on the unit's integral DX thermostat.
• Electrical/IT-room units are 24/7 — treat as critical (stage spare cooling before any swap).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
PCU-10.RUN | BI | Run status | DI dry contact | -
PCU-10.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-10.SS | BO | Start/Stop command | DO relay | - | Y
PCU-11.RUN | BI | Run status | DI dry contact | -
PCU-11.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-11.SS | BO | Start/Stop command | DO relay | - | Y
PCU-12.RUN | BI | Run status | DI dry contact | -
PCU-12.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-12.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-PKG-06
Control logic — DDC-PKG-06
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: PCU-13, PMAC-1
Strategy: Enable/monitor; integral DX (some 24/7)
Sequence of Operations
Purpose
• Packaged DX units (PCU-13, PMAC-1) — several serve IT/electrical rooms and run continuously.
Control & monitoring
• BMS enables/schedules via `*.SS` and monitors run `*.RUN` + fault `*.TRIP`; capacity is on the unit's integral DX thermostat.
• Electrical/IT-room units are 24/7 — treat as critical (stage spare cooling before any swap).
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
PCU-13.RUN | BI | Run status | DI dry contact | -
PCU-13.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PCU-13.SS | BO | Start/Stop command | DO relay | - | Y
PMAC-1.RUN | BI | Run status | DI dry contact | -
PMAC-1.TRIP | BI | Fault / alarm | DI dry contact | - |  | Y
PMAC-1.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-PKG-07
Control logic — DDC-PKG-07
Panel LCP-PKG (Packaged-unit & refrigeration panel) · B3F–B1F EPS
Equipment: REFR-1
Strategy: Start/stop + status/alarm
Sequence of Operations
Purpose
• Supervise REFR-1: start/stop, status and alarm as available.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
REFR-1.ALM1 | BI | Cold-store/refrigeration alarm — B1F 主厨房一括 | DI dry contact | - |  | Y
REFR-1.ALM2 | BI | Cold-store/refrigeration alarm — B1F 厨房冷蔵庫異常一括 | DI dry contact | - |  | Y
REFR-1.ALM3 | BI | Cold-store/refrigeration alarm — MR-1 ル・パティオ厨房 | DI dry contact | - |  | Y
REFR-1.ALM4 | BI | Cold-store/refrigeration alarm — 2F ゴミ処理室 | DI dry contact | - |  | Y
REFR-1.ALM5 | BI | Cold-store/refrigeration alarm — 2F カスケイド厨房 | DI dry contact | - |  | Y
REFR-1.ALM6 | BI | Cold-store/refrigeration alarm — 調理冷蔵庫 | DI dry contact | - |  | Y
REFR-1.ALM7 | BI | Cold-store/refrigeration alarm — 雲海厨房 | DI dry contact | - |  | Y

## DDC-LTG-01
Control logic — DDC-LTG-01
Panel LCP-LTG (Common-area & facade lighting panel) · Distributed EPS
Equipment: LTG-AVIATION, LTG-NEON, LTG-BALCONY-L
Strategy: Time/astro On-Off + status
Sequence of Operations
Purpose
• Common-area & facade lighting groups on time-program / astronomical clock.
Control
• On/Off `*.CMD` by schedule (and photocell/astro for facade); status `*.ST` proof.
Life-safety
• Aviation obstruction light: regulatory — independent circuit, dusk-to-dawn/photocell, never commanded dark; failure alarms to central.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
LTG-AVIATION.CMD | BO | On/Off command | DO relay | - | Y
LTG-AVIATION.ST | BI | Group status | DI dry contact | -
LTG-NEON.CMD | BO | On/Off command | DO relay | - | Y
LTG-NEON.ST | BI | Group status | DI dry contact | -
LTG-BALCONY-L.CMD | BO | On/Off command | DO relay | - | Y
LTG-BALCONY-L.ST | BI | Group status | DI dry contact | -

## DDC-LTG-02
Control logic — DDC-LTG-02
Panel LCP-LTG (Common-area & facade lighting panel) · Distributed EPS
Equipment: LTG-BALCONY-H, LTG-CORRIDOR, LTG-LOBBY
Strategy: Time/astro On-Off + status
Sequence of Operations
Purpose
• Common-area & facade lighting groups on time-program / astronomical clock.
Control
• On/Off `*.CMD` by schedule (and photocell/astro for facade); status `*.ST` proof.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
LTG-BALCONY-H.CMD | BO | On/Off command | DO relay | - | Y
LTG-BALCONY-H.ST | BI | Group status | DI dry contact | -
LTG-CORRIDOR.CMD | BO | On/Off command | DO relay | - | Y
LTG-CORRIDOR.ST | BI | Group status | DI dry contact | -
LTG-LOBBY.CMD | BO | On/Off command | DO relay | - | Y
LTG-LOBBY.ST | BI | Group status | DI dry contact | -

## DDC-LTG-03
Control logic — DDC-LTG-03
Panel LCP-LTG (Common-area & facade lighting panel) · Distributed EPS
Equipment: LTG-SOFFIT, LTG-TENANT
Strategy: Time/astro On-Off + status
Sequence of Operations
Purpose
• Common-area & facade lighting groups on time-program / astronomical clock.
Control
• On/Off `*.CMD` by schedule (and photocell/astro for facade); status `*.ST` proof.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
LTG-SOFFIT.CMD | BO | On/Off command | DO relay | - | Y
LTG-SOFFIT.ST | BI | Group status | DI dry contact | -
LTG-TENANT.CMD | BO | On/Off command | DO relay | - | Y
LTG-TENANT.ST | BI | Group status | DI dry contact | -

## DDC-DHW-01
Control logic — DDC-DHW-01
Panel LCP-DHW (Domestic hot-water (給湯) plant panel) · B2F / PH plant
Equipment: DHW-1, DHW-2, DHW-3
Strategy: Steam charging to storage setpoint + Legionella cycle
Sequence of Operations
Purpose
• Domestic-hot-water plant: hold stored/delivered DHW temperature per vertical zone at minimum steam use, with Legionella protection.
Control
• Modulate the steam charging valve `*.STG-CV` to hold the storage setpoint `*.STG-T` (≥60°C store / ≥55°C delivery); recirc pump `*.PMP-SS` on schedule with duty/standby.
• Meter storage steam `*.STM-M`; night/low-demand setback with a periodic thermal-disinfection cycle.
Safeties & monitoring
• High-temp / scald and low-delivery-temp alarms (`*.SUP-T`); pump fault `*.PMP-TRIP`; low-storage-temp Legionella advisory.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DHW-1.STG-T | AI | Storage-tank temperature | 4-20mA | °C | Y | Y
DHW-1.STG-CV | AO | Steam charging valve | 0-10V | % | Y
DHW-1.SUP-T | AI | DHW supply (delivery) temperature | 4-20mA | °C |  | Y
DHW-1.STM-M | AI | Storage steam-flow meter (貯湯槽蒸気流量) | Pulse/Modbus | m³
DHW-1.PMP-RUN | BI | Supply/recirc pump run status | DI dry contact | -
DHW-1.PMP-TRIP | BI | Supply/recirc pump fault | DI dry contact | - |  | Y
DHW-1.PMP-SS | BO | Supply/recirc pump start/stop | DO relay | - | Y
DHW-2.STG-T | AI | Storage-tank temperature | 4-20mA | °C | Y | Y
DHW-2.STG-CV | AO | Steam charging valve | 0-10V | % | Y
DHW-2.SUP-T | AI | DHW supply (delivery) temperature | 4-20mA | °C |  | Y
DHW-2.STM-M | AI | Storage steam-flow meter (貯湯槽蒸気流量) | Pulse/Modbus | m³
DHW-2.PMP-RUN | BI | Supply/recirc pump run status | DI dry contact | -
DHW-2.PMP-TRIP | BI | Supply/recirc pump fault | DI dry contact | - |  | Y
DHW-2.PMP-SS | BO | Supply/recirc pump start/stop | DO relay | - | Y
DHW-3.STG-T | AI | Storage-tank temperature | 4-20mA | °C | Y | Y
DHW-3.STG-CV | AO | Steam charging valve | 0-10V | % | Y
DHW-3.SUP-T | AI | DHW supply (delivery) temperature | 4-20mA | °C |  | Y
DHW-3.STM-M | AI | Storage steam-flow meter (貯湯槽蒸気流量) | Pulse/Modbus | m³
DHW-3.PMP-RUN | BI | Supply/recirc pump run status | DI dry contact | -
DHW-3.PMP-TRIP | BI | Supply/recirc pump fault | DI dry contact | - |  | Y
DHW-3.PMP-SS | BO | Supply/recirc pump start/stop | DO relay | - | Y

## DDC-DHW-02
Control logic — DDC-DHW-02
Panel LCP-DHW (Domestic hot-water (給湯) plant panel) · B2F / PH plant
Equipment: DHW-4
Strategy: Steam charging to storage setpoint + Legionella cycle
Sequence of Operations
Purpose
• Domestic-hot-water plant: hold stored/delivered DHW temperature per vertical zone at minimum steam use, with Legionella protection.
Control
• Modulate the steam charging valve `*.STG-CV` to hold the storage setpoint `*.STG-T` (≥60°C store / ≥55°C delivery); recirc pump `*.PMP-SS` on schedule with duty/standby.
• Meter storage steam `*.STM-M`; night/low-demand setback with a periodic thermal-disinfection cycle.
Safeties & monitoring
• High-temp / scald and low-delivery-temp alarms (`*.SUP-T`); pump fault `*.PMP-TRIP`; low-storage-temp Legionella advisory.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DHW-4.STG-T | AI | Storage-tank temperature | 4-20mA | °C | Y | Y
DHW-4.STG-CV | AO | Steam charging valve | 0-10V | % | Y
DHW-4.SUP-T | AI | DHW supply (delivery) temperature | 4-20mA | °C |  | Y
DHW-4.STM-M | AI | Storage steam-flow meter (貯湯槽蒸気流量) | Pulse/Modbus | m³
DHW-4.PMP-RUN | BI | Supply/recirc pump run status | DI dry contact | -
DHW-4.PMP-TRIP | BI | Supply/recirc pump fault | DI dry contact | - |  | Y
DHW-4.PMP-SS | BO | Supply/recirc pump start/stop | DO relay | - | Y

## DDC-SAN-01
Control logic — DDC-SAN-01
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: MP-1, MP-2, MP-3
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
• Lead/lag/standby across 3 booster pumps (MP-1, MP-2, MP-3): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
MP-1.RUN | BI | Run status | DI dry contact | -
MP-1.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
MP-1.SS | BO | Start/Stop command | DO relay | - | Y
MP-2.RUN | BI | Run status | DI dry contact | -
MP-2.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
MP-2.SS | BO | Start/Stop command | DO relay | - | Y
MP-3.RUN | BI | Run status | DI dry contact | -
MP-3.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
MP-3.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-SAN-02
Control logic — DDC-SAN-02
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: MP-4, P-1, P-2
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
• Lead/lag/standby across 3 booster pumps (MP-4, P-1, P-2): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
MP-4.RUN | BI | Run status | DI dry contact | -
MP-4.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
MP-4.SS | BO | Start/Stop command | DO relay | - | Y
P-1.RUN | BI | Run status | DI dry contact | -
P-1.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
P-1.SS | BO | Start/Stop command | DO relay | - | Y
P-2.RUN | BI | Run status | DI dry contact | -
P-2.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
P-2.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-SAN-03
Control logic — DDC-SAN-03
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: P-3, P-4, P-5
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
• Lead/lag/standby across 3 booster pumps (P-3, P-4, P-5): stage on demand, rotate lead on equal run-hours, prove each start before staging the next.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
P-3.RUN | BI | Run status | DI dry contact | -
P-3.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
P-3.SS | BO | Start/Stop command | DO relay | - | Y
P-4.RUN | BI | Run status | DI dry contact | -
P-4.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
P-4.SS | BO | Start/Stop command | DO relay | - | Y
P-5.RUN | BI | Run status | DI dry contact | -
P-5.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
P-5.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-SAN-04
Control logic — DDC-SAN-04
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: P-6, RCVT-1, ELVT-1
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
P-6.RUN | BI | Run status | DI dry contact | -
P-6.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
P-6.SS | BO | Start/Stop command | DO relay | - | Y
RCVT-1.LVL | AI | Potable receiving tank (上水受水槽) water level | 4-20mA | % |  | Y
RCVT-1.HI | BI | Potable receiving tank (上水受水槽) high-level alarm | DI dry contact | - |  | Y
RCVT-1.LO | BI | Potable receiving tank (上水受水槽) low-level / dry-run alarm | DI dry contact | - |  | Y
ELVT-1.LVL | AI | Potable elevated tank (高置水槽) water level | 4-20mA | % |  | Y
ELVT-1.HI | BI | Potable elevated tank (高置水槽) high-level alarm | DI dry contact | - |  | Y
ELVT-1.LO | BI | Potable elevated tank (高置水槽) low-level / dry-run alarm | DI dry contact | - |  | Y

## DDC-SAN-05
Control logic — DDC-SAN-05
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: REUSET-1, FIRET-1, DP-1
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
REUSET-1.LVL | AI | Reclaimed receiving tank (中水受水槽) water level | 4-20mA | % |  | Y
REUSET-1.HI | BI | Reclaimed receiving tank (中水受水槽) high-level alarm | DI dry contact | - |  | Y
REUSET-1.LO | BI | Reclaimed receiving tank (中水受水槽) low-level / dry-run alarm | DI dry contact | - |  | Y
FIRET-1.LVL | AI | Fire-reserve tank (消火水槽) water level | 4-20mA | % |  | Y
FIRET-1.LO | BI | Fire-reserve tank (消火水槽) low-level alarm | DI dry contact | - |  | Y
DP-1.RUN | BI | Pump run status | DI dry contact | -
DP-1.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-1.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y

## DDC-SAN-06
Control logic — DDC-SAN-06
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: DP-2, DP-3, DP-4
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DP-2.RUN | BI | Pump run status | DI dry contact | -
DP-2.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-2.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-3.RUN | BI | Pump run status | DI dry contact | -
DP-3.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-3.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-4.RUN | BI | Pump run status | DI dry contact | -
DP-4.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-4.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y

## DDC-SAN-07
Control logic — DDC-SAN-07
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: DP-5, DP-6, DP-7
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DP-5.RUN | BI | Pump run status | DI dry contact | -
DP-5.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-5.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-6.RUN | BI | Pump run status | DI dry contact | -
DP-6.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-6.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-7.RUN | BI | Pump run status | DI dry contact | -
DP-7.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-7.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y

## DDC-SAN-08
Control logic — DDC-SAN-08
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: DP-8, DP-9, DP-10
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DP-8.RUN | BI | Pump run status | DI dry contact | -
DP-8.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-8.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-9.RUN | BI | Pump run status | DI dry contact | -
DP-9.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-9.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-10.RUN | BI | Pump run status | DI dry contact | -
DP-10.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-10.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y

## DDC-SAN-09
Control logic — DDC-SAN-09
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: DP-11, DP-12, DP-13
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DP-11.RUN | BI | Pump run status | DI dry contact | -
DP-11.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-11.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-12.RUN | BI | Pump run status | DI dry contact | -
DP-12.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-12.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
DP-13.RUN | BI | Pump run status | DI dry contact | -
DP-13.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-13.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y

## DDC-SAN-10
Control logic — DDC-SAN-10
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: DP-14, BL-1-1, BL-1-2
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
DP-14.RUN | BI | Pump run status | DI dry contact | -
DP-14.TRIP | BI | Pump fault | DI dry contact | - |  | Y
DP-14.HLV | BI | High-water-level alarm | DI dry contact | - |  | Y
BL-1-1.RUN | BI | Run status | DI dry contact | -
BL-1-1.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
BL-1-1.SS | BO | Start/Stop command | DO relay | - | Y
BL-1-2.RUN | BI | Run status | DI dry contact | -
BL-1-2.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
BL-1-2.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-SAN-11
Control logic — DDC-SAN-11
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: BL-2-1, BL-2-2, BL-F-1
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
BL-2-1.RUN | BI | Run status | DI dry contact | -
BL-2-1.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
BL-2-1.SS | BO | Start/Stop command | DO relay | - | Y
BL-2-2.RUN | BI | Run status | DI dry contact | -
BL-2-2.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
BL-2-2.SS | BO | Start/Stop command | DO relay | - | Y
BL-F-1.RUN | BI | Run status | DI dry contact | -
BL-F-1.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
BL-F-1.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-SAN-12
Control logic — DDC-SAN-12
Panel LCP-SAN (Plumbing / sanitary panel (上水・中水・排水)) · B3F–B2F plant
Equipment: BL-F-2
Strategy: Lead/lag booster + float-level sump/sewage
Sequence of Operations
Purpose
• Plumbing / sanitary: maintain potable (上水) & reclaimed (中水) supply and clear drainage/sewage sumps.
Control
• Booster / transfer pumps lead/lag on tank level & pressure (`*.SS`, prove `*.RUN`); sump & sewage pumps run on float level with BMS run/high-level supervision.
• Aeration blowers cycle on DO/timer for the wastewater-treatment tanks.
Safeties & monitoring
• Tank high/low-level & dry-run alarms; sump high-water (flooding) alarm `*.HLV`; fire-reserve tank low-level is statutory; pump fault `*.TRIP`.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
BL-F-2.RUN | BI | Run status | DI dry contact | -
BL-F-2.TRIP | BI | Pump fault / breaker trip | DI dry contact | - |  | Y
BL-F-2.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-FILT-01
Control logic — DDC-FILT-01
Panel LCP-FILT (Recreational-water filtration panel (ろ過装置)) · Distributed (2F–5F)
Equipment: FILT-BATHM, FILT-BATHW, FILT-SAUNA
Strategy: Scheduled circulation + backwash
Sequence of Operations
Purpose
• Recreational-water (bath / sauna / pool / waterfall / fountain / rainwater) circulation & filtration.
Control
• Circulation pump `*.SS` on the daily schedule; periodic backwash; prove `*.RUN`, alarm `*.TRIP`; maintain turnover/turbidity per venue.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FILT-BATHM.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-BATHM.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-BATHM.SS | BO | Start/Stop command | DO relay | - | Y
FILT-BATHW.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-BATHW.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-BATHW.SS | BO | Start/Stop command | DO relay | - | Y
FILT-SAUNA.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-SAUNA.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-SAUNA.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-FILT-02
Control logic — DDC-FILT-02
Panel LCP-FILT (Recreational-water filtration panel (ろ過装置)) · Distributed (2F–5F)
Equipment: FILT-SAUNAC, FILT-OTAKI, FILT-UNKAI
Strategy: Scheduled circulation + backwash
Sequence of Operations
Purpose
• Recreational-water (bath / sauna / pool / waterfall / fountain / rainwater) circulation & filtration.
Control
• Circulation pump `*.SS` on the daily schedule; periodic backwash; prove `*.RUN`, alarm `*.TRIP`; maintain turnover/turbidity per venue.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FILT-SAUNAC.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-SAUNAC.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-SAUNAC.SS | BO | Start/Stop command | DO relay | - | Y
FILT-OTAKI.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-OTAKI.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-OTAKI.SS | BO | Start/Stop command | DO relay | - | Y
FILT-UNKAI.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-UNKAI.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-UNKAI.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-FILT-03
Control logic — DDC-FILT-03
Panel LCP-FILT (Recreational-water filtration panel (ろ過装置)) · Distributed (2F–5F)
Equipment: FILT-FOUNT, FILT-RAIN
Strategy: Scheduled circulation + backwash
Sequence of Operations
Purpose
• Recreational-water (bath / sauna / pool / waterfall / fountain / rainwater) circulation & filtration.
Control
• Circulation pump `*.SS` on the daily schedule; periodic backwash; prove `*.RUN`, alarm `*.TRIP`; maintain turnover/turbidity per venue.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
FILT-FOUNT.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-FOUNT.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-FOUNT.SS | BO | Start/Stop command | DO relay | - | Y
FILT-RAIN.RUN | BI | Circulation/filtration pump run | DI dry contact | -
FILT-RAIN.TRIP | BI | Pump / filter fault | DI dry contact | - |  | Y
FILT-RAIN.SS | BO | Start/Stop command | DO relay | - | Y

## DDC-SMK-01
Control logic — DDC-SMK-01
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-1, SMF-2, SMF-3
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-1.RUN | BI | Fan run status | DI dry contact | -
SMF-1.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-1.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-2.RUN | BI | Fan run status | DI dry contact | -
SMF-2.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-2.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-3.RUN | BI | Fan run status | DI dry contact | -
SMF-3.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-3.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-02
Control logic — DDC-SMK-02
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-4, SMF-5, SMF-6
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-4.RUN | BI | Fan run status | DI dry contact | -
SMF-4.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-4.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-5.RUN | BI | Fan run status | DI dry contact | -
SMF-5.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-5.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-6.RUN | BI | Fan run status | DI dry contact | -
SMF-6.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-6.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-03
Control logic — DDC-SMK-03
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-7, SMF-8, SMF-9
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-7.RUN | BI | Fan run status | DI dry contact | -
SMF-7.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-7.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-8.RUN | BI | Fan run status | DI dry contact | -
SMF-8.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-8.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-9.RUN | BI | Fan run status | DI dry contact | -
SMF-9.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-9.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-04
Control logic — DDC-SMK-04
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-10, SMF-11, SMF-12
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-10.RUN | BI | Fan run status | DI dry contact | -
SMF-10.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-10.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-11.RUN | BI | Fan run status | DI dry contact | -
SMF-11.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-11.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-12.RUN | BI | Fan run status | DI dry contact | -
SMF-12.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-12.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-05
Control logic — DDC-SMK-05
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-13, SMF-14, SMF-15
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-13.RUN | BI | Fan run status | DI dry contact | -
SMF-13.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-13.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-14.RUN | BI | Fan run status | DI dry contact | -
SMF-14.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-14.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-15.RUN | BI | Fan run status | DI dry contact | -
SMF-15.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-15.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-06
Control logic — DDC-SMK-06
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-16, SMF-17, SMF-18
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-16.RUN | BI | Fan run status | DI dry contact | -
SMF-16.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-16.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-17.RUN | BI | Fan run status | DI dry contact | -
SMF-17.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-17.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-18.RUN | BI | Fan run status | DI dry contact | -
SMF-18.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-18.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-07
Control logic — DDC-SMK-07
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-19, SMF-20, SMF-21
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-19.RUN | BI | Fan run status | DI dry contact | -
SMF-19.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-19.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-20.RUN | BI | Fan run status | DI dry contact | -
SMF-20.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-20.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMF-21.RUN | BI | Fan run status | DI dry contact | -
SMF-21.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-21.TRIP | BI | Fan fault | DI dry contact | - |  | Y

## DDC-SMK-08
Control logic — DDC-SMK-08
Panel LCP-SMK (Smoke-control / 排煙 panel) · Distributed / 防災
Equipment: SMF-22, SMK-FIRE
Strategy: Hard-wired fire start; BMS monitors + smoke-mode
Sequence of Operations
Purpose
• Smoke exhaust (排煙): clear smoke from the fire zone on alarm.
Life-safety control
• Life-safety start is HARD-WIRED from the disaster-prevention (fire) panel — the BMS does not gate it. On the fire batch `SMK-FIRE.ALM`, the affected `SMF-*` start and supply AHUs/dampers interlock shut.
• BMS provides monitoring (`*.RUN`, `*.TRIP`) and a supervised smoke-mode start `*.SS`; weekly/periodic run test with runtime logging.
Point schedule
Point Tag | I/O | Description | Signal / Range | Units | SP | Alarm
SMF-22.RUN | BI | Fan run status | DI dry contact | -
SMF-22.SS | BO | Smoke-mode start/stop | DO relay | -
SMF-22.TRIP | BI | Fan fault | DI dry contact | - |  | Y
SMK-FIRE.ALM | BI | Fire-alarm batch (火災一括) from disaster-prevention panel | DI dry contact | - |  | Y