## Summary
Red5-DHCP — BMS controller replacement: minimal-interruption cutover
Migrate 84 Azbil savic-net FX2 field controllers across 11 panels to new DDC in the April–May shoulder season, using OA economizer free-cooling and local manual operation to keep the hotel conditioned throughout.
Generated 2026-07-30
Field controllers to replace | 84
Field panels (+ head-end) | 11
I/O points (commissioning checklist) | 1160
Cutover window (Mar prep) | Apr–May
Why April–May | Tokyo shoulder-season OA (~10–22 °C, low enthalpy) lets the airside economizer meet the load with no mechanical cooling, so the towers (LCP-CT) and R-1 chiller are already idle and swap cold. Heating is over, so hot-water hydronics are low-risk. DHC stays live as a warm-spell safety net and is migrated last.
Enabler — local/remote | Each motor starter has a 手元/遠方 (local/remote) selector + DC24V ext start-stop + status feedback (confirmed on E-01/13-4). During a swap the equipment runs in LOCAL manual — fan hand-on, OA damper fixed ~100%, pump fixed-speed — independent of the BMS.

## Phases
Phase | Window | Panels (controllers) | Shoulder-season state | Swap method | Risk
0 | March (hot) | BMS-CENTRAL + network backbone | n/a — runs in parallel | Stand up new head-end alongside FX2; prefab panels; bench-test programs; point-verify vs I/O list | Prep
1 | early Apr | LCP-CT (8) + R-1 / condenser loop in LCP-3637 | Idle — no mechanical cooling | Power down & swap cold; recommission before any warm spell | Low
2 | April | LCP-1F (3), 2F (4), 3F (4), 4F (7) + air-side of HSL/HSH/3637 | Economizer free-cooling carries load | AHU→local, fan hand-on, OA damper ~100%; one AHU at a time; guest floors overnight | Moderate
3 | Apr–May | LCP-HSL (17), LCP-HSH (11) — pumps / HX / hydronics | Heating off; only trickle CHW needed | One pump local fixed-speed / manual bypass; duty & standby never both down | Moderate
4 | May (last) | LCP-DHC (7) — DHC chilled-water + steam intake | Primary source; economizer covers building | DHC valves/pumps to local manual + district coordination; low-occupancy weekend | Critical
A | any time | LCP-PKG (7) — IT / electrical-room packaged DX | Runs 24/7 (not seasonal) | DX to local thermostat; fast one-at-a-time; spare/portable cooling staged | Critical
B | any time | LCP-LTG (3) — common-area & facade lighting | Runs to schedule | Local switch/override; aviation obstruction light on independent circuit — never dark | Moderate

## Playbook
System | Local-mode setup while BMS is disconnected | Watch-out
AHU / OAU fans | COS→手元, fan hand-ON, OA damper fixed ~100% (economizer), DHC coil valve left manually crackable | Warm spell → be able to open the cooling valve within minutes
CHW / HW pumps | One pump hand-ON at fixed speed; DP/bypass set manually | Keep duty OR standby always available; protect domestic-hot-water continuity
Cooling towers / condenser / R-1 | Leave isolated & de-energised | None — off-season; recommission before enabling mechanical cooling
DHC intake | Intake isolation + energy valves and pumps to local manual, fixed position | Primary source — coordinate with district operator; do this phase last
Packaged units (IT/elec rooms) | DX on local thermostat, continuous run | 24/7 critical rooms — stage spare/portable cooling; swap one unit at a time
Lighting | Local switching / manual override per circuit | Aviation obstruction light is regulatory life-safety — independent circuit, always lit

## Risks
Control | Detail
Cutover discipline | Only one system in manual at any time. Guest-facing zones swapped overnight, back-of-house first. Old controller stays landed on a marshalling strip so you can revert to FX2 within minutes. Freeze all scope changes during the window; spares on site.
Never interrupt | Life-safety interlocks — smoke control, stair pressurization, exhaust — remain live and coordinated with the fire-alarm system. Aviation obstruction light and IT/electrical-room cooling stay energised.
Verify every point | The 1,160-point I/O list is the master checklist. Per controller: point-to-point verify each AI/AO/BI/BO, functional-test, then trend 24–48 h before returning to auto.
Weather safety net | DHC stays operational until Phase 4, so a warm spell is covered. The sequence guarantees the building always has either economizer free-cooling or the DHC source available.