## Summary
Red5-DHCP — Power-panel / MCC schedule (ESCO retrofit)
PH1F machine-room 動力制御盤 feeders for the RC-1 (36/37F) chiller and the new CP-8 DHC chilled-water pump. Source: E-01 / E-02 / 13-4 動力盤改造図.
Generated 2026-07-30 · source: E-01 / E-02 / 13-4 動力盤改造図
Panels | 3
Circuits | 7
Connected load (kW) | 90.7
Panel | Name | Location | Supply | Circuits | Note
P-PH1-1 | 動力制御盤 P-PH1-1 (Power/motor-control panel) | PH1F machine room | 3φ3W 400V | 1 | Existing panel; CP-8 chilled-water-pump circuit newly added under the ESCO works.
P-PH1-2 | 動力制御盤 P-PH1-2 (Power/motor-control panel) | PH1F machine room | 3φ3W 400V | 2 | Existing panel modified; 600AF main + revenue/sub kWh meter; feeds the new RC-1 local switch panel.
LSP-RC1 | 手元開閉器盤 (RC-1用) — RC-1 local switch/disconnect panel | PH1F machine room (adjacent RC-1 / 36-37F chiller) | 3φ3W 400V from P-PH1-2 | 4 | New local panel for the RC-1 (Ebara twin-screw) chiller: one feeder per compressor + two spare feeders.

## Schedule
Panel | Location | Supply | Circuit | Load / served | kW | Protective device | Feeder cable | Metering / control | Work
P-PH1-1 — 動力制御盤 P-PH1-1 (Power/motor-control panel) | PH1F machine room | 3φ3W 400V
P-PH1-1 | PH1F machine room | 3φ3W 400V | CP-8 | CP-8 冷水ポンプ (DHC-side CHW pump) | 3.7 | ELCB 3P 30AF/20AT (MWS-CV) + MS (MSO-N21) + THR 2.2–5A | CV3.5sq-4C (∅ 22) | WH 20/5A 1kWh-pulse → BMS; local/remote COS; ext start-stop DC24V; run/fault status out | New
P-PH1-2 — 動力制御盤 P-PH1-2 (Power/motor-control panel) | PH1F machine room | 3φ3W 400V
P-PH1-2 | PH1F machine room | 3φ3W 400V | MAIN | Panel incomer / main breaker |  | MCCB 3P 600AF/600AT | CVT100sq-E14 (existing conduit reused) | WH 200/5A 1kWh-pulse → BMS | Modify
P-PH1-2 | PH1F machine room | 3φ3W 400V | F-RC1 | Feeder → 手元開閉器盤 (RC-1用) local panel |  | MCCB 3P 250AF/200AT | CVT100sq-E14 | — | Modify
LSP-RC1 — 手元開閉器盤 (RC-1用) — RC-1 local switch/disconnect panel | PH1F machine room (adjacent RC-1 / 36-37F chiller) | 3φ3W 400V from P-PH1-2
LSP-RC1 | PH1F machine room (adjacent RC-1 / 36-37F chiller) | 3φ3W 400V from P-PH1-2 | RC-1(1) | 36/37F chiller RC-1 — compressor #1 | 43.5 | MCCB 3P 250AF/150AT | CVT22sq-E5.5 | Chiller-integral control; BMS run/alarm + kW | New
LSP-RC1 | PH1F machine room (adjacent RC-1 / 36-37F chiller) | 3φ3W 400V from P-PH1-2 | RC-1(2) | 36/37F chiller RC-1 — compressor #2 | 43.5 | MCCB 3P 250AF/150AT | CVT22sq-E5.5 | Chiller-integral control; BMS run/alarm + kW | New
LSP-RC1 | PH1F machine room (adjacent RC-1 / 36-37F chiller) | 3φ3W 400V from P-PH1-2 | SP-1 | 予備電源 (spare feeder 1) |  | MCCB 3P 50AF/30AT | CV5.5sq-3C | — | New
LSP-RC1 | PH1F machine room (adjacent RC-1 / 36-37F chiller) | 3φ3W 400V from P-PH1-2 | SP-2 | 予備電源 (spare feeder 2) |  | MCCB 3P 50AF/30AT | CV5.5sq-3C | — | New