## Cover
Red5-DHCP — BMS I/O List & Panel / Controller Schedule
ANA InterContinental Tokyo — District Heating & Cooling (DHC) connected hotel BMS
Building | SRC, B3–37F, ~98,331 m²; Azbil savic-net FX / FX2 BMS
Energy source | District Heating & Cooling (PRIMARY): DHC chilled-water intake (冷水受入 CS/CR, GJ metered) + DHC steam (蒸気受入 SS 0.8→0.2 MPa, condensate HR to hot-well). Local plant is backup/peaking.
Distribution | Low-rise (低層): CP-1 ×3 CHW + HP-1 ×3 HW pumps, EX-2 laundry HX. High-rise (高層): CP-2 ×3 CHW + HP-2 ×3 HW, CP-3(INV)/CP-6, EX-3 HX. Expansion EXT-1/2; OA stations ST-1/ST-2.
36/37F local plant | R-1 single water-cooled SCREW chiller (Ebara RHS DW202M2, 370 kW / 82.2 kW in / COP 4.5, twin 45 kW screw comp, R-407C) in changeover with DHC via HEX-1 + CP-8; CDP-3 + CT-3 condenser; CP-7 CHW; HP-4 + EX4 + EXT-3 secondary; 2 source-changeover valves
Condenser water | CT-1 (2 INV cells) + CT-2 (2 cells + filtration) + CDP-1 ×3 / CDP-2 ×2 pumps rejecting heat from packaged units (PCU/PAC/PMAC) & kitchen refrigeration; EX-1 winter free-cooling; 2 emergency cooling HX to DHC
Air side | AC-1..27 AHUs (public/kitchen), EVU-1..15 outdoor-air units, guest-room FCU zone-groups (5-20F & 21-35F × N/NE/SE/S/SW, 4-pipe) + 36/37F FCU, EF/SF/RF fans
Also on savic-net | Packaged units PCU/PAC/PMAC (status/alarm), kitchen refrigeration alarms, common-area/facade lighting (照明一覧)
ESCO control scope | Pump optimization, outdoor-air-unit optimization, thermal-demand control (per 共-01 spec)
BMS platform | Azbil savic-net FX2, S/W 機能仕様 dated 2015/04/09 — confirmed from the 144-page Azbil 納入仕様書 (software function spec, not an equipment list)
Sheets | Panels · Controllers · IO_List (+ Phys. panel/floor cross-ref) · IO_Summary · Reconciliation · Points-by-Floor · LCP-to-Physical · Delta-Controllers · Legend
Basis | Azbil 完成図 savic-net graphics (熱源設備 全体/低層/高層/36,37F/冷却塔/ホットウェル/DHC受入, graphs 1000-1100; PMAC-PAC & 照明一覧), air-side summary graphs (空調関連/客室等), M-* CAD equipment schedules, 共-01 ESCO spec, 空調機スケジュール_20251127.xlsx
Note | Device tags/counts read directly from the savic-net graphics. Per-unit packaged (PCU/PAC/PMAC) and per-floor lighting lists are modelled as representative supervised groups — expand from 照明一覧1/2 + PMAC/PAC一覧 for the full point count.

## Panels
Panel ID | Description | Location | Areas / Systems served | Controllers | I/O points
BMS-CENTRAL | Azbil savic-net FX2 central monitoring (中央監視) | B2F Central Monitoring Rm | Whole-building supervisory on savic-net FX2 (S/W spec 2015/04/09): point mgmt, start-stop/setpoint operation, status & alarm/event processing, time-program + calendar + event-program control, seasonal changeover (batch), remote-setpoint schedules, runtime/start-count & deviation/hi-lo limit monitoring, trend + periodic data collection, daily/monthly reports, energy CSV export, numeric/logic operations, power-failure/restoration handling, user/access mgmt, maintenance & spare-parts mgmt | 0 | 0
LCP-DHC | DHC intake & hot-well panel | B2F Machine Room | DHC chilled-water intake (CS/CR, GJ meter), DHC steam intake (SS 8k->2k, HR condensate), hot-well HWT-1 + HP-5 condensate-return / HP-3 kitchen pumps, main energy meters | 7 | 56
LCP-CT | Cooling-tower & condenser-water panel | Rooftop / PH | CT-1/CT-2 cells (INV), CDP-1/CDP-2 condenser pumps, EX-1 winter free-cooling HX, emergency cooling HX to DHC; serves packaged units & kitchen refrigeration heat rejection | 8 | 83
LCP-HSL | Low-rise distribution panel (低層系統) | B2F Machine Room | CP-1 primary CHW x3, HP-1 hot-water x3, CP-4/CP-5 kitchen pumps, EX-2 laundry HX, EXT-1, ST-1 OA station; low-rise AC/EVU + 5~20F FCU headers | 17 | 222
LCP-HSH | High-rise distribution panel (高層系統) | PH Machine Room | CP-2 primary CHW x3, HP-2 hot-water x3, CP-3(INV)/CP-6 pumps, EX-3 HX, EXT-2, ST-2 OA station; high-rise AC/EVU + 21~35F FCU headers | 11 | 182
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | 37F PH Machine Room | R-1 chiller + CDP-3 + CT-3 condenser, CP-7 CHW pumps, HEX-1 + CP-8 DHC HX, EX4 + HP-4 secondary + EXT-3, DHC<->R-1 changeover valves; 36/37F AC/EVU/FCU | 13 | 171
LCP-1F | 1F–2F air-side panel | 1F EPS/AHU Room | AC-7, EVU-1..3 (1F ceremony/banquet/lobby) | 3 | 54
LCP-2F | 2F air-side panel | 2F AHU Room | AC-8..13, EVU-4..6 (atrium, Prominence, offices/tenants) | 4 | 117
LCP-3F | 3F air-side panel | 3F AHU Room | AC-14..16, EVU-7 (Unkai/Karin/DaVinci, chapel) | 4 | 68
LCP-4F | 4F–5F air-side panel | 4F AHU Room | AC-17..21, EVU-8..10 (kitchens, low-rise guest-room OAUs) | 7 | 133
LCP-PKG | Packaged-unit & refrigeration panel | B3F–B1F EPS | PCU/PAC/PMAC packaged air-conditioners (status/alarm), kitchen refrigeration/cold-store alarms | 7 | 58
LCP-LTG | Common-area & facade lighting panel | Distributed EPS | Facade (aviation light, neon, balcony) + per-floor common-area lighting groups (照明一覧) | 3 | 16

## Controllers
Controller ID | Panel | Type | Devices served | Point count
DDC-DHC-01 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | DHC-CHW | 10
DDC-DHC-02 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | DHC-STEAM | 7
DDC-DHC-03 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | HWT-1 | 5
DDC-DHC-04 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | HP-5-1, HP-5-2, HP-3-1 | 21
DDC-DHC-05 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | HP-3-2 | 7
DDC-DHC-06 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | MTR-ELEC-MAIN, MTR-GAS-MAIN, MTR-WATER-MAIN | 3
DDC-DHC-07 | LCP-DHC | DDC field controller (Azbil Infilex/savic-net class) | MTR-DHC-CHW, MTR-DHC-STEAM, MTR-DHC-COND | 3
DDC-CT-01 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | CT-1-1, CT-1-2, CT-1 | 16
DDC-CT-02 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | CT-2-1, CT-2-2, CT-2 | 18
DDC-CT-03 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | CT-3-1, CT-3 | 11
DDC-CT-04 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | CDP-1-1, CDP-1-2, CDP-1-3 | 12
DDC-CT-05 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | CDP-2-1, CDP-2-2, CDP-3-1 | 12
DDC-CT-06 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | CDP-3-2 | 4
DDC-CT-07 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | EX-1, EMHX-1, EMHX-2 | 9
DDC-CT-08 | LCP-CT | DDC field controller (Azbil Infilex/savic-net class) | MTR-CDW-KWH | 1
DDC-HSL-01 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | EX-2-1, EX-2-2 | 8
DDC-HSL-02 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | CP-1-1, CP-1-2, CP-1-3 | 21
DDC-HSL-03 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | CP-4-1, CP-4-2, CP-5-1 | 21
DDC-HSL-04 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | CP-5-2 | 7
DDC-HSL-05 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | HP-1-1, HP-1-2, HP-1-3 | 21
DDC-HSL-06 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | EXT-1 | 3
DDC-HSL-07 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | ST-1 | 3
DDC-HSL-08 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | AC-1, AC-2, AC-3 | 29
DDC-HSL-09 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | AC-4, AC-5, AC-6 | 34
DDC-HSL-10 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | AC-26 | 12
DDC-HSL-11 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | FCU-L-N, FCU-L-NE, FCU-L-SE | 21
DDC-HSL-12 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | FCU-L-S, FCU-L-SW | 14
DDC-HSL-13 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | SF-6, EF-28, EF-32 | 9
DDC-HSL-14 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | EF-33, EF-97, RF-7 | 9
DDC-HSL-15 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | RF-8, RF-9 | 6
DDC-HSL-16 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | POOL-FP | 3
DDC-HSL-17 | LCP-HSL | DDC field controller (Azbil Infilex/savic-net class) | MTR-AHU-KWH | 1
DDC-HSH-01 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | EX-3-1, EX-3-2 | 8
DDC-HSH-02 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | CP-2-1, CP-2-2, CP-2-3 | 21
DDC-HSH-03 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | CP-3-1, CP-3-2, CP-6-1 | 21
DDC-HSH-04 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | CP-6-2 | 7
DDC-HSH-05 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | HP-2-1, HP-2-2, HP-2-3 | 21
DDC-HSH-06 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | EXT-2 | 3
DDC-HSH-07 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | ST-2 | 3
DDC-HSH-08 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | EVU-11, EVU-12, EVU-13 | 39
DDC-HSH-09 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | EVU-14, EVU-15 | 24
DDC-HSH-10 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | FCU-H-N, FCU-H-NE, FCU-H-SE | 21
DDC-HSH-11 | LCP-HSH | DDC field controller (Azbil Infilex/savic-net class) | FCU-H-S, FCU-H-SW | 14
DDC-3637-01 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | R-1 | 10
DDC-3637-02 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | HEX-1 | 7
DDC-3637-03 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | CP-7-1, CP-7-2, CP-8-1 | 21
DDC-3637-04 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | CP-8-2, CP-8-3 | 14
DDC-3637-05 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | HP-4-1, HP-4-2 | 14
DDC-3637-06 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | EX4, EXT-3 | 7
DDC-3637-07 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | CHGV-1, CHGV-2 | 4
DDC-3637-08 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | AC-22, AC-23, AC-24 | 38
DDC-3637-09 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | AC-25, AC-27 | 26
DDC-3637-10 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | FCU-3637 | 7
DDC-3637-11 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | EF-82, EF-83, EF-84 | 11
DDC-3637-12 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | EF-85, EF-86, EF-89 | 9
DDC-3637-13 | LCP-3637 | DDC field controller (Azbil Infilex/savic-net class) | EF-98 | 3
DDC-1F-01 | LCP-1F | DDC field controller (Azbil Infilex/savic-net class) | AC-7 | 12
DDC-1F-02 | LCP-1F | DDC field controller (Azbil Infilex/savic-net class) | EVU-1, EVU-2, EVU-3 | 36
DDC-1F-03 | LCP-1F | DDC field controller (Azbil Infilex/savic-net class) | EF-41, EF-42 | 6
DDC-2F-01 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | AC-8, AC-9, AC-10 | 36
DDC-2F-02 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | AC-11, AC-12, AC-13 | 36
DDC-2F-03 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | EVU-4, EVU-5, EVU-6 | 36
DDC-2F-04 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | EF-2-1, EF-46, EF-47 | 9
DDC-3F-01 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | AC-14, AC-15, AC-16 | 38
DDC-3F-02 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | EVU-7 | 12
DDC-3F-03 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | EF-56, EF-60, EF-61 | 9
DDC-3F-04 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | EF-62, EF-76, EF-77 | 9
DDC-4F-01 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | AC-17, AC-18, AC-19 | 38
DDC-4F-02 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | AC-20, AC-21 | 24
DDC-4F-03 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EVU-8, EVU-9, EVU-10 | 39
DDC-4F-04 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-54, EF-55, EF-57 | 9
DDC-4F-05 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-58, EF-59, EF-59-2 | 9
DDC-4F-06 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-67, EF-69, EF-70 | 11
DDC-4F-07 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-71 | 3
DDC-PKG-01 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | PAC-1-1, PAC-1-2, PAC-2 | 9
DDC-PKG-02 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | PAC-3, PAC-4, PAC-5 | 9
DDC-PKG-03 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | PCU-1-1, PCU-1-2, PCU-5 | 9
DDC-PKG-04 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | PCU-6, PCU-7, PCU-8 | 9
DDC-PKG-05 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | PCU-10, PCU-11, PCU-12 | 9
DDC-PKG-06 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | PCU-13, PMAC-1 | 6
DDC-PKG-07 | LCP-PKG | DDC field controller (Azbil Infilex/savic-net class) | REFR-1 | 7
DDC-LTG-01 | LCP-LTG | DDC field controller (Azbil Infilex/savic-net class) | LTG-AVIATION, LTG-NEON, LTG-BALCONY-L | 6
DDC-LTG-02 | LCP-LTG | DDC field controller (Azbil Infilex/savic-net class) | LTG-BALCONY-H, LTG-CORRIDOR, LTG-LOBBY | 6
DDC-LTG-03 | LCP-LTG | DDC field controller (Azbil Infilex/savic-net class) | LTG-SOFFIT, LTG-TENANT | 4

## IO_List
Point Tag | System | Device ID | Device Type | Area / Served | Panel | Controller | Phys. panel (26.07.30) | Phys. floor | Point Description | I/O Type | Signal / Range | Units | SP/Sched | Alarm | Trend | Notes / Basis
DHC-CHW.CS-T | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Supply (CS) temp | AI | 4-20mA | °C |  | Y | Y | DHC冷水受入 ~7°C
DHC-CHW.CR-T | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Return (CR) temp | AI | 4-20mA | °C |  |  | Y | DHC冷水返送
DHC-CHW.CS-P | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Supply header pressure | AI | 4-20mA | MPa |  | Y | Y
DHC-CHW.CR-P | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Return header pressure | AI | 4-20mA | MPa |  |  | Y
DHC-CHW.FLW | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Intake flow | AI | 4-20mA | m³/h |  |  | Y
DHC-CHW.GJ | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Thermal-energy meter | AI | Pulse/Modbus | GJ |  |  | Y | GJ/h + integrated; thermal-demand control
DHC-CHW.CV | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Intake control valve | AO | 0-10V | % | Y |  |  | Modulate to building load
DHC-CHW.CVFB | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Intake valve position fb | AI | 4-20mA | %
DHC-CHW.ISOL | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Intake isolation valve open/close | BO | DO relay | - | Y
DHC-CHW.ISOL-ST | DHC interface | DHC-CHW | DHC chilled-water intake | B2F DHC chilled-water intake (CS/CR headers) | LCP-DHC | DDC-DHC-01 |  |  | Isolation valve status | BI | DI dry contact | - |  | Y
DHC-STEAM.SS-P | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | Supply (SS 8k) pressure | AI | 4-20mA | MPa |  | Y | Y | ~0.8 MPa
DHC-STEAM.MASS | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | Steam mass-flow meter | AI | Pulse/Modbus | t/h |  |  | Y | t/h + integrated kg
DHC-STEAM.PRV | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | PRV 8k->2k reducing valve | AO | 0-10V | % | Y |  |  | 0.8->0.2 MPa
DHC-STEAM.SSH2-P | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | Reduced (SSH 2k) pressure | AI | 4-20mA | MPa |  |  | Y | ~0.2 MPa
DHC-STEAM.ISOL | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | Main isolation valve open/close | BO | DO relay | - | Y |  |  | Season enable + OA lockout
DHC-STEAM.ISOL-ST | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | Isolation valve status | BI | DI dry contact | - |  | Y
DHC-STEAM.HR-M | DHC interface | DHC-STEAM | DHC steam intake | B2F DHC steam intake (SS 8k->2k / HR) | LCP-DHC | DDC-DHC-02 |  |  | Condensate (HR) return meter | AI | Pulse/Modbus | L |  |  | Y | Hot-return to DHC via HWT-1
HWT-1.LVL | Heat source | HWT-1 | Hot-well / condensate tank | B2F hot-well room | LCP-DHC | DDC-DHC-03 |  |  | Tank level | AI | 4-20mA | % |  | Y | Y
HWT-1.HI | Heat source | HWT-1 | Hot-well / condensate tank | B2F hot-well room | LCP-DHC | DDC-DHC-03 |  |  | High-level alarm | BI | DI dry contact | - |  | Y
HWT-1.LO | Heat source | HWT-1 | Hot-well / condensate tank | B2F hot-well room | LCP-DHC | DDC-DHC-03 |  |  | Low-level alarm | BI | DI dry contact | - |  | Y
HWT-1.T | Heat source | HWT-1 | Hot-well / condensate tank | B2F hot-well room | LCP-DHC | DDC-DHC-03 |  |  | Condensate temp | AI | 4-20mA | °C |  |  | Y
HWT-1.MU | Heat source | HWT-1 | Hot-well / condensate tank | B2F hot-well room | LCP-DHC | DDC-DHC-03 |  |  | Make-up water valve | BO | DO relay | -
HP-5-1.RUN | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-5-1.TRIP | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-5-1.SS | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Start/Stop command | BO | DO relay | -
HP-5-1.SPD | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-5; HWT-1 -> DHC hot-return
HP-5-1.SPDFB | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-5-1.KW | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-5-1.FLW | Heat source | HP-5-1 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-5-2.RUN | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-5-2.TRIP | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-5-2.SS | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Start/Stop command | BO | DO relay | -
HP-5-2.SPD | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-5; HWT-1 -> DHC hot-return
HP-5-2.SPDFB | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-5-2.KW | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-5-2.FLW | Heat source | HP-5-2 | Condensate-return pump (to DHC) | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-3-1.RUN | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-3-1.TRIP | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-3-1.SS | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Start/Stop command | BO | DO relay | -
HP-3-1.SPD | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-3; serves B1F 厨房 AC-5/6/7
HP-3-1.SPDFB | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-3-1.KW | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-3-1.FLW | Heat source | HP-3-1 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-3-2.RUN | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-3-2.TRIP | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-3-2.SS | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | Start/Stop command | BO | DO relay | -
HP-3-2.SPD | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-3; serves B1F 厨房 AC-5/6/7
HP-3-2.SPDFB | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-3-2.KW | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-3-2.FLW | Heat source | HP-3-2 | Kitchen-AHU hot-water pump | B2F hot-well room | LCP-DHC | DDC-DHC-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CT-1-1.RUN | Condenser water | CT-1-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan run status | BI | DI dry contact | - |  |  | Y
CT-1-1.TRIP | Condenser water | CT-1-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan INV fault | BI | DI dry contact | - |  | Y
CT-1-1.SS | Condenser water | CT-1-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan start/stop | BO | DO relay | -
CT-1-1.SPD | Condenser water | CT-1-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-1-1.SPDFB | Condenser water | CT-1-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-1-2.RUN | Condenser water | CT-1-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan run status | BI | DI dry contact | - |  |  | Y
CT-1-2.TRIP | Condenser water | CT-1-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan INV fault | BI | DI dry contact | - |  | Y
CT-1-2.SS | Condenser water | CT-1-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan start/stop | BO | DO relay | -
CT-1-2.SPD | Condenser water | CT-1-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-1-2.SPDFB | Condenser water | CT-1-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-01 |  |  | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-1.LVL | Condenser water | CT-1 | Cooling tower | Rooftop | LCP-CT | DDC-CT-01 |  |  | Basin water level | AI | 4-20mA | % |  | Y
CT-1.MU | Condenser water | CT-1 | Cooling tower | Rooftop | LCP-CT | DDC-CT-01 |  |  | Make-up water valve | BO | DO relay | -
CT-1.BLD | Condenser water | CT-1 | Cooling tower | Rooftop | LCP-CT | DDC-CT-01 |  |  | Bleed/blowdown valve | BO | DO relay | -
CT-1.DRY | Condenser water | CT-1 | Cooling tower | Rooftop | LCP-CT | DDC-CT-01 |  |  | Low-water (渇水) alarm | BI | DI dry contact | - |  | Y
CT-1.CHEM | Condenser water | CT-1 | Cooling tower | Rooftop | LCP-CT | DDC-CT-01 |  |  | Chemical dosing (薬注) batch fault | BI | DI dry contact | - |  | Y
CT-1.EH | Condenser water | CT-1 | Cooling tower | Rooftop | LCP-CT | DDC-CT-01 |  |  | Basin heater (E/H) enable | BO | DO relay | - |  |  |  | Freeze protection
CT-2-1.RUN | Condenser water | CT-2-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan run status | BI | DI dry contact | - |  |  | Y
CT-2-1.TRIP | Condenser water | CT-2-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan INV fault | BI | DI dry contact | - |  | Y
CT-2-1.SS | Condenser water | CT-2-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan start/stop | BO | DO relay | -
CT-2-1.SPD | Condenser water | CT-2-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-2-1.SPDFB | Condenser water | CT-2-1 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-2-2.RUN | Condenser water | CT-2-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan run status | BI | DI dry contact | - |  |  | Y
CT-2-2.TRIP | Condenser water | CT-2-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan INV fault | BI | DI dry contact | - |  | Y
CT-2-2.SS | Condenser water | CT-2-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan start/stop | BO | DO relay | -
CT-2-2.SPD | Condenser water | CT-2-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-2-2.SPDFB | Condenser water | CT-2-2 | Cooling tower cell | Rooftop | LCP-CT | DDC-CT-02 |  |  | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-2.LVL | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Basin water level | AI | 4-20mA | % |  | Y
CT-2.MU | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Make-up water valve | BO | DO relay | -
CT-2.BLD | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Bleed/blowdown valve | BO | DO relay | -
CT-2.DRY | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Low-water (渇水) alarm | BI | DI dry contact | - |  | Y
CT-2.CHEM | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Chemical dosing (薬注) batch fault | BI | DI dry contact | - |  | Y
CT-2.EH | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Basin heater (E/H) enable | BO | DO relay | - |  |  |  | Freeze protection
CT-2.FILT-RUN | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Filtration (ろ過) pump run | BI | DI dry contact | - |  |  | Y
CT-2.FILT-SS | Condenser water | CT-2 | Cooling tower | Rooftop | LCP-CT | DDC-CT-02 |  |  | Filtration pump start/stop | BO | DO relay | -
CDP-1-1.RUN | Condenser water | CDP-1-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-1-1.TRIP | Condenser water | CDP-1-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-1-1.SS | Condenser water | CDP-1-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-1-1.FLW | Condenser water | CDP-1-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CDP-1-2.RUN | Condenser water | CDP-1-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-1-2.TRIP | Condenser water | CDP-1-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-1-2.SS | Condenser water | CDP-1-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-1-2.FLW | Condenser water | CDP-1-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CDP-1-3.RUN | Condenser water | CDP-1-3 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-1-3.TRIP | Condenser water | CDP-1-3 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-1-3.SS | Condenser water | CDP-1-3 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-1-3.FLW | Condenser water | CDP-1-3 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CDP-2-1.RUN | Condenser water | CDP-2-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-2-1.TRIP | Condenser water | CDP-2-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-2-1.SS | Condenser water | CDP-2-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-2-1.FLW | Condenser water | CDP-2-1 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CDP-2-2.RUN | Condenser water | CDP-2-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-2-2.TRIP | Condenser water | CDP-2-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-2-2.SS | Condenser water | CDP-2-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-2-2.FLW | Condenser water | CDP-2-2 | Condenser-water pump | Condenser-water plant | LCP-CT | DDC-CT-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
EX-1.EN | Condenser water | EX-1 | Free-cooling HX (winter) | Rooftop (winter free-cooling) | LCP-CT | DDC-CT-07 |  |  | Free-cooling enable / changeover | BO | DO relay | - | Y |  |  | Low wet-bulb winter free-cooling
EX-1.ST | Condenser water | EX-1 | Free-cooling HX (winter) | Rooftop (winter free-cooling) | LCP-CT | DDC-CT-07 |  |  | CHW-side leaving temp | AI | 4-20mA | °C |  |  | Y
EX-1.CV | Condenser water | EX-1 | Free-cooling HX (winter) | Rooftop (winter free-cooling) | LCP-CT | DDC-CT-07 |  |  | CW-side control valve | AO | 0-10V | % | Y
EMHX-1.EN | Condenser water | EMHX-1 | Emergency cooling HX (to DHC) | Low-floor emergency cooling (to DHC) | LCP-CT | DDC-CT-07 |  |  | Emergency cooling enable | BO | DO relay | - | Y |  |  | 低層階非常用; from DHC冷水受入ヘッダ
EMHX-1.ST | Condenser water | EMHX-1 | Emergency cooling HX (to DHC) | Low-floor emergency cooling (to DHC) | LCP-CT | DDC-CT-07 |  |  | Cooling-water leaving temp | AI | 4-20mA | °C |  |  | Y
EMHX-1.ISOL | Condenser water | EMHX-1 | Emergency cooling HX (to DHC) | Low-floor emergency cooling (to DHC) | LCP-CT | DDC-CT-07 |  |  | DHC-side isolation valve | BO | DO relay | -
EMHX-2.EN | Condenser water | EMHX-2 | Emergency cooling HX (to DHC) | Low-floor emergency cooling (to DHC) | LCP-CT | DDC-CT-07 |  |  | Emergency cooling enable | BO | DO relay | - | Y |  |  | 低層階非常用; from DHC冷水受入ヘッダ
EMHX-2.ST | Condenser water | EMHX-2 | Emergency cooling HX (to DHC) | Low-floor emergency cooling (to DHC) | LCP-CT | DDC-CT-07 |  |  | Cooling-water leaving temp | AI | 4-20mA | °C |  |  | Y
EMHX-2.ISOL | Condenser water | EMHX-2 | Emergency cooling HX (to DHC) | Low-floor emergency cooling (to DHC) | LCP-CT | DDC-CT-07 |  |  | DHC-side isolation valve | BO | DO relay | -
ST-1.T | Common | ST-1 | Outdoor-air station | Low-rise OA station | LCP-HSL | DDC-HSL-07 |  |  | Outdoor dry-bulb temp | AI | 4-20mA | °C |  |  | Y | 低層 OA sensor
ST-1.RH | Common | ST-1 | Outdoor-air station | Low-rise OA station | LCP-HSL | DDC-HSL-07 |  |  | Outdoor humidity | AI | 4-20mA | %RH |  |  | Y
ST-1.WB | Common | ST-1 | Outdoor-air station | Low-rise OA station | LCP-HSL | DDC-HSL-07 |  |  | Wet-bulb temp (計測/演算) | AI | 4-20mA | °C |  |  | Y | Drives CW setpoint + free-cooling
CP-1-1.RUN | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-1-1.TRIP | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-1-1.SS | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Start/Stop command | BO | DO relay | -
CP-1-1.SPD | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-1; sequenced/群起動; VFD; DP-reset
CP-1-1.SPDFB | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-1-1.KW | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-1-1.FLW | Heat source | CP-1-1 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-1-2.RUN | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-1-2.TRIP | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-1-2.SS | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Start/Stop command | BO | DO relay | -
CP-1-2.SPD | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-1; sequenced/群起動; VFD; DP-reset
CP-1-2.SPDFB | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-1-2.KW | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-1-2.FLW | Heat source | CP-1-2 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-1-3.RUN | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-1-3.TRIP | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-1-3.SS | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Start/Stop command | BO | DO relay | -
CP-1-3.SPD | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-1; sequenced/群起動; VFD; DP-reset
CP-1-3.SPDFB | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-1-3.KW | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-1-3.FLW | Heat source | CP-1-3 | Primary CHW pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-02 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-1-1.RUN | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-1-1.TRIP | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-1-1.SS | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Start/Stop command | BO | DO relay | -
HP-1-1.SPD | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-1; sequenced; 4-pipe heating loop
HP-1-1.SPDFB | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-1-1.KW | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-1-1.FLW | Heat source | HP-1-1 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-1-2.RUN | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-1-2.TRIP | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-1-2.SS | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Start/Stop command | BO | DO relay | -
HP-1-2.SPD | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-1; sequenced; 4-pipe heating loop
HP-1-2.SPDFB | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-1-2.KW | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-1-2.FLW | Heat source | HP-1-2 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-1-3.RUN | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-1-3.TRIP | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-1-3.SS | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Start/Stop command | BO | DO relay | -
HP-1-3.SPD | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-1; sequenced; 4-pipe heating loop
HP-1-3.SPDFB | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-1-3.KW | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-1-3.FLW | Heat source | HP-1-3 | Hot-water pump (low-rise) | B2F machine room | LCP-HSL | DDC-HSL-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-4-1.RUN | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-4-1.TRIP | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-4-1.SS | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Start/Stop command | BO | DO relay | -
CP-4-1.SPD | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-4; open/close + duty rotation
CP-4-1.SPDFB | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-4-1.KW | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-4-1.FLW | Heat source | CP-4-1 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-4-2.RUN | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-4-2.TRIP | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-4-2.SS | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Start/Stop command | BO | DO relay | -
CP-4-2.SPD | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-4; open/close + duty rotation
CP-4-2.SPDFB | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-4-2.KW | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-4-2.FLW | Heat source | CP-4-2 | B1F kitchen CHW pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-5-1.RUN | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-5-1.TRIP | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-5-1.SS | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Start/Stop command | BO | DO relay | -
CP-5-1.SPD | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-5
CP-5-1.SPDFB | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-5-1.KW | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-5-1.FLW | Heat source | CP-5-1 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-5-2.RUN | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-5-2.TRIP | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-5-2.SS | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | Start/Stop command | BO | DO relay | -
CP-5-2.SPD | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-5
CP-5-2.SPDFB | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-5-2.KW | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-5-2.FLW | Heat source | CP-5-2 | B1F kitchen pump | B2F machine room | LCP-HSL | DDC-HSL-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
EX-2-1.P-IN | Heat source | EX-2-1 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Primary inlet temp (laundry) | AI | 4-20mA | °C |  |  | Y
EX-2-1.S-OUT | Heat source | EX-2-1 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Secondary outlet (supply) temp | AI | 4-20mA | °C | Y | Y | Y
EX-2-1.PV | Heat source | EX-2-1 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
EX-2-1.PVFB | Heat source | EX-2-1 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Primary valve position fb | AI | 4-20mA | %
EX-2-2.P-IN | Heat source | EX-2-2 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Primary inlet temp (laundry) | AI | 4-20mA | °C |  |  | Y
EX-2-2.S-OUT | Heat source | EX-2-2 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Secondary outlet (supply) temp | AI | 4-20mA | °C | Y | Y | Y
EX-2-2.PV | Heat source | EX-2-2 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
EX-2-2.PVFB | Heat source | EX-2-2 | Plate heat exchanger | B2F (laundry) | LCP-HSL | DDC-HSL-01 |  |  | Primary valve position fb | AI | 4-20mA | %
EXT-1.LVL | Heat source | EXT-1 | Expansion tank | B2F machine room (low-rise) | LCP-HSL | DDC-HSL-06 |  |  | Tank level | AI | 4-20mA | % |  | Y | Y
EXT-1.HI | Heat source | EXT-1 | Expansion tank | B2F machine room (low-rise) | LCP-HSL | DDC-HSL-06 |  |  | High-level alarm | BI | DI dry contact | - |  | Y
EXT-1.LO | Heat source | EXT-1 | Expansion tank | B2F machine room (low-rise) | LCP-HSL | DDC-HSL-06 |  |  | Low-level alarm | BI | DI dry contact | - |  | Y
ST-2.T | Common | ST-2 | Outdoor-air station | High-rise OA station | LCP-HSH | DDC-HSH-07 |  |  | Outdoor dry-bulb temp | AI | 4-20mA | °C |  |  | Y | 高層 OA sensor
ST-2.RH | Common | ST-2 | Outdoor-air station | High-rise OA station | LCP-HSH | DDC-HSH-07 |  |  | Outdoor humidity | AI | 4-20mA | %RH |  |  | Y
ST-2.WB | Common | ST-2 | Outdoor-air station | High-rise OA station | LCP-HSH | DDC-HSH-07 |  |  | Wet-bulb temp (計測/演算) | AI | 4-20mA | °C |  |  | Y | Drives CW setpoint + free-cooling
CP-2-1.RUN | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-2-1.TRIP | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-2-1.SS | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Start/Stop command | BO | DO relay | -
CP-2-1.SPD | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-2; sequenced/群起動; VFD; DP-reset
CP-2-1.SPDFB | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-2-1.KW | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-2-1.FLW | Heat source | CP-2-1 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-2-2.RUN | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-2-2.TRIP | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-2-2.SS | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Start/Stop command | BO | DO relay | -
CP-2-2.SPD | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-2; sequenced/群起動; VFD; DP-reset
CP-2-2.SPDFB | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-2-2.KW | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-2-2.FLW | Heat source | CP-2-2 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-2-3.RUN | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-2-3.TRIP | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-2-3.SS | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Start/Stop command | BO | DO relay | -
CP-2-3.SPD | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-2; sequenced/群起動; VFD; DP-reset
CP-2-3.SPDFB | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-2-3.KW | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-2-3.FLW | Heat source | CP-2-3 | Primary CHW pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-02 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-2-1.RUN | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-2-1.TRIP | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-2-1.SS | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Start/Stop command | BO | DO relay | -
HP-2-1.SPD | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-2; sequenced; 4-pipe heating loop
HP-2-1.SPDFB | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-2-1.KW | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-2-1.FLW | Heat source | HP-2-1 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-2-2.RUN | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-2-2.TRIP | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-2-2.SS | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Start/Stop command | BO | DO relay | -
HP-2-2.SPD | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-2; sequenced; 4-pipe heating loop
HP-2-2.SPDFB | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-2-2.KW | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-2-2.FLW | Heat source | HP-2-2 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-2-3.RUN | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-2-3.TRIP | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-2-3.SS | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Start/Stop command | BO | DO relay | -
HP-2-3.SPD | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-2; sequenced; 4-pipe heating loop
HP-2-3.SPDFB | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-2-3.KW | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-2-3.FLW | Heat source | HP-2-3 | Hot-water pump (high-rise) | PH machine room | LCP-HSH | DDC-HSH-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-3-1.RUN | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-3-1.TRIP | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-3-1.SS | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Start/Stop command | BO | DO relay | -
CP-3-1.SPD | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-3; INV; control-flow l/m
CP-3-1.SPDFB | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-3-1.KW | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-3-1.FLW | Heat source | CP-3-1 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-3-2.RUN | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-3-2.TRIP | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-3-2.SS | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Start/Stop command | BO | DO relay | -
CP-3-2.SPD | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-3; INV; control-flow l/m
CP-3-2.SPDFB | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-3-2.KW | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-3-2.FLW | Heat source | CP-3-2 | High-rise CHW pump (INV) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-6-1.RUN | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-6-1.TRIP | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-6-1.SS | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Start/Stop command | BO | DO relay | -
CP-6-1.SPD | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-6; 順序切替 ON:№1優先
CP-6-1.SPDFB | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-6-1.KW | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-6-1.FLW | Heat source | CP-6-1 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-6-2.RUN | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-6-2.TRIP | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-6-2.SS | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | Start/Stop command | BO | DO relay | -
CP-6-2.SPD | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-6; 順序切替 ON:№1優先
CP-6-2.SPDFB | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-6-2.KW | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-6-2.FLW | Heat source | CP-6-2 | High-rise pump (seq changeover) | PH machine room | LCP-HSH | DDC-HSH-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
EX-3-1.P-IN | Heat source | EX-3-1 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Primary inlet temp (kitchen) | AI | 4-20mA | °C |  |  | Y
EX-3-1.S-OUT | Heat source | EX-3-1 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Secondary outlet (supply) temp | AI | 4-20mA | °C | Y | Y | Y
EX-3-1.PV | Heat source | EX-3-1 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
EX-3-1.PVFB | Heat source | EX-3-1 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Primary valve position fb | AI | 4-20mA | %
EX-3-2.P-IN | Heat source | EX-3-2 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Primary inlet temp (kitchen) | AI | 4-20mA | °C |  |  | Y
EX-3-2.S-OUT | Heat source | EX-3-2 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Secondary outlet (supply) temp | AI | 4-20mA | °C | Y | Y | Y
EX-3-2.PV | Heat source | EX-3-2 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
EX-3-2.PVFB | Heat source | EX-3-2 | Plate heat exchanger | PH (high-rise kitchen) | LCP-HSH | DDC-HSH-01 |  |  | Primary valve position fb | AI | 4-20mA | %
EXT-2.LVL | Heat source | EXT-2 | Expansion tank | PH machine room (high-rise) | LCP-HSH | DDC-HSH-06 |  |  | Tank level | AI | 4-20mA | % |  | Y | Y
EXT-2.HI | Heat source | EXT-2 | Expansion tank | PH machine room (high-rise) | LCP-HSH | DDC-HSH-06 |  |  | High-level alarm | BI | DI dry contact | - |  | Y
EXT-2.LO | Heat source | EXT-2 | Expansion tank | PH machine room (high-rise) | LCP-HSH | DDC-HSH-06 |  |  | Low-level alarm | BI | DI dry contact | - |  | Y
R-1.RUN | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Run status | BI | DI dry contact | - |  |  | Y
R-1.TRIP | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Common fault / trip | BI | DI dry contact | - |  | Y
R-1.LR | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Local/Remote status | BI | DI dry contact | -
R-1.SS | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 36/37F local chiller; BACKUP to DHC (チラーバックアップ); source changeover valves
R-1.DMD | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Capacity/demand limit | AO | 0-10V | % | Y |  |  | Demand-limit / soft-load
R-1.CHWST | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | CHW supply (leaving) temp | AI | 4-20mA | °C |  | Y | Y | Design 7°C
R-1.CHWRT | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | CHW return (entering) temp | AI | 4-20mA | °C |  |  | Y | Design 12°C
R-1.CWRT | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Condenser water leaving temp | AI | 4-20mA | °C |  |  | Y
R-1.KW | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Electrical input power | AI | 4-20mA | kW |  |  | Y | Ebara screw RHS DW202M2: 370 kW cool / 82.2 kW in (COP 4.5); 2×45 kW screw comp, R-407C
R-1.FLW | Heat source | R-1 | Water-cooled screw chiller (local backup) | 37F PH machine room | LCP-3637 | DDC-3637-01 |  |  | Evaporator flow proof | BI | DI dry contact | - |  | Y
CDP-3-1.RUN | Condenser water | CDP-3-1 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-3-1.TRIP | Condenser water | CDP-3-1 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-05 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-3-1.SS | Condenser water | CDP-3-1 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-05 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-3-1.FLW | Condenser water | CDP-3-1 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CDP-3-2.RUN | Condenser water | CDP-3-2 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-06 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CDP-3-2.TRIP | Condenser water | CDP-3-2 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-06 |  |  | Fault / breaker trip | BI | DI dry contact | - |  | Y
CDP-3-2.SS | Condenser water | CDP-3-2 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-06 |  |  | Start/Stop command | BO | DO relay | - |  |  |  | Group start (群起動); interlock w/ CT + load
CDP-3-2.FLW | Condenser water | CDP-3-2 | Condenser-water pump | 37F PH (R-1 condenser) | LCP-CT | DDC-CT-06 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CT-3-1.RUN | Condenser water | CT-3-1 | Cooling tower cell | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Fan run status | BI | DI dry contact | - |  |  | Y
CT-3-1.TRIP | Condenser water | CT-3-1 | Cooling tower cell | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Fan INV fault | BI | DI dry contact | - |  | Y
CT-3-1.SS | Condenser water | CT-3-1 | Cooling tower cell | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Fan start/stop | BO | DO relay | -
CT-3-1.SPD | Condenser water | CT-3-1 | Cooling tower cell | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-3-1.SPDFB | Condenser water | CT-3-1 | Cooling tower cell | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-3.LVL | Condenser water | CT-3 | Cooling tower | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Basin water level | AI | 4-20mA | % |  | Y
CT-3.MU | Condenser water | CT-3 | Cooling tower | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Make-up water valve | BO | DO relay | -
CT-3.BLD | Condenser water | CT-3 | Cooling tower | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Bleed/blowdown valve | BO | DO relay | -
CT-3.DRY | Condenser water | CT-3 | Cooling tower | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Low-water (渇水) alarm | BI | DI dry contact | - |  | Y
CT-3.CHEM | Condenser water | CT-3 | Cooling tower | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Chemical dosing (薬注) batch fault | BI | DI dry contact | - |  | Y
CT-3.EH | Condenser water | CT-3 | Cooling tower | 37F PH (R-1) | LCP-CT | DDC-CT-03 |  |  | Basin heater (E/H) enable | BO | DO relay | - |  |  |  | Freeze protection
CP-7-1.RUN | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-7-1.TRIP | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-7-1.SS | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Start/Stop command | BO | DO relay | -
CP-7-1.SPD | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-7; duty/standby; 発停/故障
CP-7-1.SPDFB | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-7-1.KW | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-7-1.FLW | Heat source | CP-7-1 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-7-2.RUN | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-7-2.TRIP | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-7-2.SS | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Start/Stop command | BO | DO relay | -
CP-7-2.SPD | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-7; duty/standby; 発停/故障
CP-7-2.SPDFB | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-7-2.KW | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-7-2.FLW | Heat source | CP-7-2 | R-1 CHW primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-4-1.RUN | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-4-1.TRIP | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-4-1.SS | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Start/Stop command | BO | DO relay | -
HP-4-1.SPD | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-4; EX4 secondary -> FCU/AC/EVU
HP-4-1.SPDFB | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-4-1.KW | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-4-1.FLW | Heat source | HP-4-1 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HP-4-2.RUN | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
HP-4-2.TRIP | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
HP-4-2.SS | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Start/Stop command | BO | DO relay | -
HP-4-2.SPD | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | HP-4; EX4 secondary -> FCU/AC/EVU
HP-4-2.SPDFB | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HP-4-2.KW | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Power | AI | 4-20mA | kW |  |  | Y
HP-4-2.FLW | Heat source | HP-4-2 | 36/37F secondary loop pump | 37F PH machine room | LCP-3637 | DDC-3637-05 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
HEX-1.P-IN | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | Primary (DHC) inlet temp | AI | 4-20mA | °C |  |  | Y | 36/37F DHC tie-in (チラーバックアップ)
HEX-1.P-OUT | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | Primary (DHC) outlet temp | AI | 4-20mA | °C |  |  | Y
HEX-1.S-OUT | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | Secondary (loop) supply temp | AI | 4-20mA | °C | Y | Y | Y | Loop CHW setpoint
HEX-1.S-FLW | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | Secondary supply flow | AI | 4-20mA | m³/h |  |  | Y
HEX-1.GJ | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | DHC thermal-energy meter | AI | Pulse/Modbus | MJ |  |  | Y | m³/h + MJ on the graphic
HEX-1.PV | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
HEX-1.PVFB | Heat source | HEX-1 | DHC chilled-water plate HX | 37F PH machine room | LCP-3637 | DDC-3637-02 |  |  | Primary valve position fb | AI | 4-20mA | %
CP-8-1.RUN | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-8-1.TRIP | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-8-1.SS | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Start/Stop command | BO | DO relay | -
CP-8-1.SPD | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-8; DHC side of HEX-1; metered
CP-8-1.SPDFB | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-8-1.KW | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-8-1.FLW | Heat source | CP-8-1 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-03 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-8-2.RUN | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-8-2.TRIP | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-8-2.SS | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Start/Stop command | BO | DO relay | -
CP-8-2.SPD | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-8; DHC side of HEX-1; metered
CP-8-2.SPDFB | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-8-2.KW | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-8-2.FLW | Heat source | CP-8-2 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-8-3.RUN | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
CP-8-3.TRIP | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-8-3.SS | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Start/Stop command | BO | DO relay | -
CP-8-3.SPD | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | VFD speed command | AO | 0-10V | % | Y |  |  | CP-8; DHC side of HEX-1; metered
CP-8-3.SPDFB | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-8-3.KW | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Power | AI | 4-20mA | kW |  |  | Y
CP-8-3.FLW | Heat source | CP-8-3 | HEX-1 (DHC) primary pump | 37F PH machine room | LCP-3637 | DDC-3637-04 |  |  | Flow/DP proof | BI | DI dry contact | - |  | Y
EX4.P-IN | Heat source | EX4 | Plate heat exchanger | 37F PH (source/secondary buffer) | LCP-3637 | DDC-3637-06 |  |  | Primary inlet temp (36/37F loop) | AI | 4-20mA | °C |  |  | Y
EX4.S-OUT | Heat source | EX4 | Plate heat exchanger | 37F PH (source/secondary buffer) | LCP-3637 | DDC-3637-06 |  |  | Secondary outlet (supply) temp | AI | 4-20mA | °C | Y | Y | Y
EX4.PV | Heat source | EX4 | Plate heat exchanger | 37F PH (source/secondary buffer) | LCP-3637 | DDC-3637-06 |  |  | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
EX4.PVFB | Heat source | EX4 | Plate heat exchanger | 37F PH (source/secondary buffer) | LCP-3637 | DDC-3637-06 |  |  | Primary valve position fb | AI | 4-20mA | %
EXT-3.LVL | Heat source | EXT-3 | Expansion tank | 37F PH machine room | LCP-3637 | DDC-3637-06 |  |  | Tank level | AI | 4-20mA | % |  | Y | Y
EXT-3.HI | Heat source | EXT-3 | Expansion tank | 37F PH machine room | LCP-3637 | DDC-3637-06 |  |  | High-level alarm | BI | DI dry contact | - |  | Y
EXT-3.LO | Heat source | EXT-3 | Expansion tank | 37F PH machine room | LCP-3637 | DDC-3637-06 |  |  | Low-level alarm | BI | DI dry contact | - |  | Y
CHGV-1.CMD | Heat source | CHGV-1 | Source-changeover valve | 37F PH (R-1 branch) | LCP-3637 | DDC-3637-07 |  |  | Open/close command | BO | DO relay | - | Y |  |  | R-1 evaporator branch valve (open = chiller mode)
CHGV-1.ST | Heat source | CHGV-1 | Source-changeover valve | 37F PH (R-1 branch) | LCP-3637 | DDC-3637-07 |  |  | Position status | BI | DI dry contact | - |  | Y
CHGV-2.CMD | Heat source | CHGV-2 | Source-changeover valve | 37F PH (through-main) | LCP-3637 | DDC-3637-07 |  |  | Open/close command | BO | DO relay | - | Y |  |  | Through-main valve (open = DHC bypass mode)
CHGV-2.ST | Heat source | CHGV-2 | Source-changeover valve | 37F PH (through-main) | LCP-3637 | DDC-3637-07 |  |  | Position status | BI | DI dry contact | - |  | Y
AC-1.RUN | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-1.TRIP | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-1.SS | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-1.SPD | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-1.SAT | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-1.RAT | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-1.CCV | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-1.HCV | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-1.FLT | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-1.OAD | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Outdoor-air damper | AO | 0-10V | % | Y
AC-1.FRZ | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-HSL | DDC-HSL-08 | RCP-B3-1 | B3F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-2.RUN | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-2.TRIP | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-2.SS | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-2.SPD | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-2.SAT | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-2.RAT | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-2.CCV | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-2.FLT | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-2.OAD | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-HSL | DDC-HSL-08 | RCP-B1-2 | B1F | Outdoor-air damper | AO | 0-10V | % | Y
AC-3.RUN | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-3.TRIP | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-3.SS | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-3.SPD | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-3.SAT | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-3.RAT | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-3.CCV | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-3.FLT | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-3.OAD | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-HSL | DDC-HSL-08 | RCP-B2-1 | B2F | Outdoor-air damper | AO | 0-10V | % | Y
AC-4.RUN | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-4.TRIP | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-4.SS | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-4.SPD | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-4.SPDFB | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-4.SAT | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-4.RAT | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-4.CCV | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-4.FLT | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-4.OAD | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-HSL | DDC-HSL-09 | RCP-B1-3 | B1F | Outdoor-air damper | AO | 0-10V | % | Y
AC-5.RUN | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-5.TRIP | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-5.SS | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-5.SPD | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-5.SPDFB | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-5.SAT | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-5.RAT | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-5.CCV | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-5.HCV | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-5.FLT | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-5.OAD | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Outdoor-air damper | AO | 0-10V | % | Y
AC-5.FRZ | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-1 | B1F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-6.RUN | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-6.TRIP | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-6.SS | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-6.SPD | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-6.SPDFB | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-6.SAT | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-6.RAT | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-6.CCV | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-6.HCV | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-6.FLT | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-6.OAD | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Outdoor-air damper | AO | 0-10V | % | Y
AC-6.FRZ | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-HSL | DDC-HSL-09 | RCP-B1-2 | B1F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-7.RUN | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-7.TRIP | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-7.SS | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-7.SPD | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-7.SPDFB | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-7.SAT | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-7.RAT | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-7.CCV | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-7.HCV | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-7.FLT | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-7.OAD | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Outdoor-air damper | AO | 0-10V | % | Y
AC-7.FRZ | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | RCP-1-2 | 1F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-8.RUN | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-8.TRIP | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
AC-8.SS | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-8.SPD | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-8.SAT | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-8.RAT | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-8.CCV | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-8.HCV | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-8.FLT | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-8.OAD | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Outdoor-air damper | AO | 0-10V | % | Y
AC-8.FRZ | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-9.RUN | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-9.TRIP | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
AC-9.SS | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-9.SPD | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-9.SAT | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-9.RAT | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-9.CCV | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-9.HCV | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-9.FLT | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-9.OAD | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Outdoor-air damper | AO | 0-10V | % | Y
AC-9.FRZ | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-10.RUN | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-10.TRIP | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
AC-10.SS | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-10.SPD | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-10.SPDFB | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-10.SAT | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-10.RAT | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-10.CCV | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-10.HCV | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-10.HUM | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Steam humidifier valve | AO | 0-10V | % | Y
AC-10.RH | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-10.FLT | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-10.OAD | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Outdoor-air damper | AO | 0-10V | % | Y
AC-10.FRZ | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-11.RUN | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-11.TRIP | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-11.SS | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-11.SPD | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-11.SPDFB | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-11.SAT | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-11.RAT | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-11.CCV | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-11.HCV | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-11.FLT | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-11.OAD | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Outdoor-air damper | AO | 0-10V | % | Y
AC-11.FRZ | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-12.RUN | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-12.TRIP | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-12.SS | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-12.SPD | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-12.SPDFB | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-12.SAT | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-12.RAT | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-12.CCV | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-12.HCV | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-12.FLT | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-12.OAD | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Outdoor-air damper | AO | 0-10V | % | Y
AC-12.FRZ | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-13.RUN | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-13.TRIP | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-13.SS | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-13.SPD | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-13.SPDFB | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-13.SAT | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-13.RAT | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-13.CCV | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-13.HCV | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-13.FLT | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-13.OAD | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Outdoor-air damper | AO | 0-10V | % | Y
AC-13.FRZ | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | RCP-2-2 | 2F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-14.RUN | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-14.TRIP | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-14.SS | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-14.SPD | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-14.SPDFB | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-14.SAT | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-14.RAT | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-14.CCV | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-14.HCV | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-14.HUM | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Steam humidifier valve | AO | 0-10V | % | Y
AC-14.RH | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-14.FLT | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-14.OAD | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Outdoor-air damper | AO | 0-10V | % | Y
AC-14.FRZ | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | RCP-3-1 | 3F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-15.RUN | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-15.TRIP | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-15.SS | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-15.SPD | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-15.SPDFB | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-15.SAT | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-15.RAT | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-15.CCV | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-15.HCV | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-15.FLT | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-15.OAD | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Outdoor-air damper | AO | 0-10V | % | Y
AC-15.FRZ | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-16.RUN | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-16.TRIP | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-16.SS | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-16.SPD | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-16.SPDFB | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-16.SAT | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-16.RAT | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-16.CCV | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-16.HCV | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-16.FLT | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-16.OAD | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Outdoor-air damper | AO | 0-10V | % | Y
AC-16.FRZ | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | RCP-3-2 | 3F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-17.RUN | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-17.TRIP | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-17.SS | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-17.SPD | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-17.SPDFB | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-17.SAT | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-17.RAT | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-17.CCV | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-17.HCV | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-17.FLT | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-17.OAD | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Outdoor-air damper | AO | 0-10V | % | Y
AC-17.FRZ | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | RCP-4-2 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-18.RUN | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-18.TRIP | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-18.SS | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-18.SPD | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-18.SPDFB | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-18.SAT | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-18.RAT | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-18.CCV | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-18.HCV | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-18.FLT | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-18.OAD | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Outdoor-air damper | AO | 0-10V | % | Y
AC-18.FRZ | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-19.RUN | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-19.TRIP | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-19.SS | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-19.SPD | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-19.SPDFB | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-19.SAT | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-19.RAT | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-19.CCV | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-19.HCV | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-19.HUM | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Steam humidifier valve | AO | 0-10V | % | Y
AC-19.RH | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-19.FLT | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-19.OAD | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Outdoor-air damper | AO | 0-10V | % | Y
AC-19.FRZ | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | RCP-4-4 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-20.RUN | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-20.TRIP | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-20.SS | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-20.SPD | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-20.SPDFB | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-20.SAT | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-20.RAT | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-20.CCV | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-20.HCV | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-20.FLT | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-20.OAD | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Outdoor-air damper | AO | 0-10V | % | Y
AC-20.FRZ | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | RCP-4-3 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-21.RUN | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-21.TRIP | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-21.SS | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-21.SPD | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-21.SPDFB | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-21.SAT | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-21.RAT | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-21.CCV | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-21.HCV | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-21.FLT | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-21.OAD | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Outdoor-air damper | AO | 0-10V | % | Y
AC-21.FRZ | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | RCP-4-2 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-22.RUN | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-22.TRIP | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-22.SS | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-22.SPD | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-22.SPDFB | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-22.SAT | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-22.RAT | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-22.CCV | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-22.HCV | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-22.FLT | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-22.OAD | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Outdoor-air damper | AO | 0-10V | % | Y
AC-22.FRZ | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-23.RUN | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-23.TRIP | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-23.SS | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-23.SPD | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-23.SPDFB | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-23.SAT | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-23.RAT | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-23.CCV | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-23.HCV | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-23.FLT | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-23.OAD | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Outdoor-air damper | AO | 0-10V | % | Y
AC-23.FRZ | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-3637 | DDC-3637-08 | RCP-PH1-1 | PH1 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-24.RUN | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-24.TRIP | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-24.SS | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-24.SPD | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-24.SPDFB | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-24.SAT | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-24.RAT | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-24.CCV | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-24.HCV | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-24.HUM | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Steam humidifier valve | AO | 0-10V | % | Y
AC-24.RH | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-24.FLT | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-24.OAD | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Outdoor-air damper | AO | 0-10V | % | Y
AC-24.FRZ | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-3637 | DDC-3637-08 | RCP-PH1-2 | PH1 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-25.RUN | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-25.TRIP | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
AC-25.SS | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-25.SPD | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-25.SPDFB | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-25.SAT | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-25.RAT | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-25.CCV | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-25.HCV | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-25.FLT | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-25.OAD | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Outdoor-air damper | AO | 0-10V | % | Y
AC-25.FRZ | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-3637 | DDC-3637-09 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-26.RUN | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-26.TRIP | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Supply fan fault | BI | DI dry contact | - |  | Y
AC-26.SS | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-26.SPD | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-26.SPDFB | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-26.SAT | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-26.RAT | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-26.CCV | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-26.HCV | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-26.FLT | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-26.OAD | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Outdoor-air damper | AO | 0-10V | % | Y
AC-26.FRZ | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-HSL | DDC-HSL-10 | CP-B2-3 | B2F | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-27.RUN | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-27.TRIP | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
AC-27.SS | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-27.SPD | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-27.SPDFB | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-27.SAT | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-27.RAT | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-27.CCV | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-27.HCV | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-27.HUM | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Steam humidifier valve | AO | 0-10V | % | Y
AC-27.RH | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-27.FLT | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-27.OAD | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Outdoor-air damper | AO | 0-10V | % | Y
AC-27.FRZ | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-3637 | DDC-3637-09 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-1.RUN | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-1.TRIP | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-1.SS | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-1.SPD | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-1.SAT | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-1.OAT | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-1.OARH | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-1.CCV | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-1.HCV | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-1.HUM | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-1.FLT | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-1.FRZ | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | RCP-1-1 | 1F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-2.RUN | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-2.TRIP | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-2.SS | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-2.SPD | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-2.SAT | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-2.OAT | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-2.OARH | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-2.CCV | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-2.HCV | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-2.HUM | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-2.FLT | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-2.FRZ | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | RCP-1-2 | 1F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-3.RUN | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-3.TRIP | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-3.SS | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-3.SPD | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-3.SAT | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-3.OAT | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-3.OARH | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-3.CCV | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-3.HCV | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-3.HUM | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-3.FLT | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-3.FRZ | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | RCP-1-3 | 1F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-4.RUN | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-4.TRIP | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-4.SS | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-4.SPD | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-4.SAT | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-4.OAT | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-4.OARH | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-4.CCV | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-4.HCV | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-4.HUM | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-4.FLT | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-4.FRZ | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-5.RUN | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-5.TRIP | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-5.SS | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-5.SPD | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-5.SAT | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-5.OAT | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-5.OARH | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-5.CCV | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-5.HCV | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-5.HUM | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-5.FLT | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-5.FRZ | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | RCP-2-2 | 2F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-6.RUN | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-6.TRIP | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-6.SS | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-6.SPD | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-6.SAT | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-6.OAT | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-6.OARH | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-6.CCV | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-6.HCV | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-6.HUM | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Steam humidifier valve | AO | 0-10V | % | Y
EVU-6.FLT | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-6.FRZ | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-7.RUN | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-7.TRIP | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-7.SS | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-7.SPD | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-7.SAT | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-7.OAT | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-7.OARH | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-7.CCV | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-7.HCV | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-7.HUM | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-7.FLT | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-7.FRZ | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | RCP-3-2 | 3F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-8.RUN | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-8.TRIP | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-8.SS | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-8.SPD | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-8.SPDFB | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-8.SAT | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-8.OAT | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-8.OARH | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-8.CCV | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-8.HCV | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-8.HUM | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-8.FLT | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-8.FRZ | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-1 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-9.RUN | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-9.TRIP | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-9.SS | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-9.SPD | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-9.SPDFB | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-9.SAT | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-9.OAT | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-9.OARH | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-9.CCV | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-9.HCV | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-9.HUM | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-9.FLT | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-9.FRZ | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-2 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-10.RUN | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-10.TRIP | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-10.SS | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-10.SPD | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-10.SPDFB | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-10.SAT | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-10.OAT | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-10.OARH | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-10.CCV | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-10.HCV | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-10.HUM | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Steam humidifier valve | AO | 0-10V | % | Y
EVU-10.FLT | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-10.FRZ | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | RCP-4-3 | 4F | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-11.RUN | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-11.TRIP | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-11.SS | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-11.SPD | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-11.SPDFB | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-11.SAT | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-11.OAT | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-11.OARH | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-11.CCV | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-11.HCV | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-11.HUM | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-11.FLT | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-11.FRZ | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-12.RUN | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-12.TRIP | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-12.SS | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-12.SPD | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-12.SPDFB | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-12.SAT | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-12.OAT | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-12.OARH | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-12.CCV | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-12.HCV | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-12.HUM | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Steam humidifier valve | AO | 0-10V | % | Y
EVU-12.FLT | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-12.FRZ | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-HSH | DDC-HSH-08 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-13.RUN | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-13.TRIP | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-13.SS | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-13.SPD | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-13.SPDFB | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-13.SAT | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-13.OAT | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-13.OARH | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-13.CCV | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-13.HCV | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-13.HUM | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-13.FLT | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-13.FRZ | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-HSH | DDC-HSH-08 | RCP-PH1-2 | PH1 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-14.RUN | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-14.TRIP | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-14.SS | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-14.SPD | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-14.SAT | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-14.OAT | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-14.OARH | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-14.CCV | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-14.HCV | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-14.HUM | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Steam humidifier valve | AO | 0-10V | % | Y
EVU-14.FLT | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-14.FRZ | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-HSH | DDC-HSH-09 |  |  | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-15.RUN | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-15.TRIP | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-15.SS | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-15.SPD | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-15.SAT | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-15.OAT | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-15.OARH | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-15.CCV | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-15.HCV | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-15.HUM | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-15.FLT | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-15.FRZ | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-HSH | DDC-HSH-09 | RCP-PH1-1 | PH1 | Freeze protection stat | BI | DI dry contact | - |  | Y
FCU-L-N.EN | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-N.MODE | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-N.CWV | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-N.HWV | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-N.CWBV-F | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-N.HWBV-F | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-N.RT | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-HSL | DDC-HSL-11 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-NE.EN | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-NE.MODE | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-NE.CWV | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-NE.HWV | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-NE.CWBV-F | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-NE.HWBV-F | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-NE.RT | Air side | FCU-L-NE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (NE) | LCP-HSL | DDC-HSL-11 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-SE.EN | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-SE.MODE | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-SE.CWV | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-SE.HWV | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-SE.CWBV-F | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-SE.HWBV-F | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-SE.RT | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-HSL | DDC-HSL-11 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-S.EN | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-S.MODE | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-S.CWV | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-S.HWV | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-S.CWBV-F | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-S.HWBV-F | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-S.RT | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-HSL | DDC-HSL-12 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-SW.EN | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-SW.MODE | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-SW.CWV | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-SW.HWV | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-SW.CWBV-F | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-SW.HWBV-F | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-SW.RT | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-HSL | DDC-HSL-12 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-N.EN | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-N.MODE | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-N.CWV | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-N.HWV | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-N.CWBV-F | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-N.HWBV-F | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-N.RT | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (N) | LCP-HSH | DDC-HSH-10 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-NE.EN | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-NE.MODE | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-NE.CWV | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-NE.HWV | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-NE.CWBV-F | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-NE.HWBV-F | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-NE.RT | Air side | FCU-H-NE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (NE) | LCP-HSH | DDC-HSH-10 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-SE.EN | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-SE.MODE | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-SE.CWV | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-SE.HWV | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-SE.CWBV-F | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-SE.HWBV-F | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-SE.RT | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SE) | LCP-HSH | DDC-HSH-10 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-S.EN | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-S.MODE | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-S.CWV | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-S.HWV | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-S.CWBV-F | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-S.HWBV-F | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-S.RT | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (S) | LCP-HSH | DDC-HSH-11 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-SW.EN | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-SW.MODE | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-SW.CWV | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-SW.HWV | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-SW.CWBV-F | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-SW.HWBV-F | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-SW.RT | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 21-35F (SW) | LCP-HSH | DDC-HSH-11 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-3637.EN | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Group enable / schedule | BO | DO relay | - | Y |  |  | 36/37F: EX4 secondary loop (DHC/R-1 source)
FCU-3637.MODE | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-3637.CWV | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Chilled-water group valve | AO | 0-10V | % | Y
FCU-3637.HWV | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-3637.CWBV-F | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-3637.HWBV-F | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-3637.RT | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe, EX4 secondary loop) | LCP-3637 | DDC-3637-10 |  |  | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
SF-6.SS | Ventilation | SF-6 | Exhaust/supply fan | Serves AC-1 (B3-4F service elevator hall) | LCP-HSL | DDC-HSL-13 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
SF-6.RUN | Ventilation | SF-6 | Exhaust/supply fan | Serves AC-1 (B3-4F service elevator hall) | LCP-HSL | DDC-HSL-13 |  |  | Run status | BI | DI dry contact | - |  |  | Y
SF-6.TRIP | Ventilation | SF-6 | Exhaust/supply fan | Serves AC-1 (B3-4F service elevator hall) | LCP-HSL | DDC-HSL-13 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-2-1.SS | Ventilation | EF-2-1 | Exhaust/supply fan | Serves AC-8 (Cascade Cafe hall) | LCP-2F | DDC-2F-04 | RCP-B3-2 | B3F | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-2-1.RUN | Ventilation | EF-2-1 | Exhaust/supply fan | Serves AC-8 (Cascade Cafe hall) | LCP-2F | DDC-2F-04 | RCP-B3-2 | B3F | Run status | BI | DI dry contact | - |  |  | Y
EF-2-1.TRIP | Ventilation | EF-2-1 | Exhaust/supply fan | Serves AC-8 (Cascade Cafe hall) | LCP-2F | DDC-2F-04 | RCP-B3-2 | B3F | Fault | BI | DI dry contact | - |  | Y
EF-28.SS | Ventilation | EF-28 | Exhaust/supply fan | Serves AC-5 (Guardmanger & Bakery kitchen) | LCP-HSL | DDC-HSL-13 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-28.RUN | Ventilation | EF-28 | Exhaust/supply fan | Serves AC-5 (Guardmanger & Bakery kitchen) | LCP-HSL | DDC-HSL-13 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-28.TRIP | Ventilation | EF-28 | Exhaust/supply fan | Serves AC-5 (Guardmanger & Bakery kitchen) | LCP-HSL | DDC-HSL-13 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-32.SS | Ventilation | EF-32 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-HSL | DDC-HSL-13 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-32.RUN | Ventilation | EF-32 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-HSL | DDC-HSL-13 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-32.TRIP | Ventilation | EF-32 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-HSL | DDC-HSL-13 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-33.SS | Ventilation | EF-33 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-HSL | DDC-HSL-14 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-33.RUN | Ventilation | EF-33 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-HSL | DDC-HSL-14 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-33.TRIP | Ventilation | EF-33 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-HSL | DDC-HSL-14 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-41.SS | Ventilation | EF-41 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-41.RUN | Ventilation | EF-41 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-41.TRIP | Ventilation | EF-41 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-42.SS | Ventilation | EF-42 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-42.RUN | Ventilation | EF-42 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-42.TRIP | Ventilation | EF-42 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-46.SS | Ventilation | EF-46 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-46.RUN | Ventilation | EF-46 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-46.TRIP | Ventilation | EF-46 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-47.SS | Ventilation | EF-47 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-47.RUN | Ventilation | EF-47 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-47.TRIP | Ventilation | EF-47 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-54.SS | Ventilation | EF-54 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-54.RUN | Ventilation | EF-54 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-54.TRIP | Ventilation | EF-54 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-55.SS | Ventilation | EF-55 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-55.RUN | Ventilation | EF-55 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-55.TRIP | Ventilation | EF-55 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-56.SS | Ventilation | EF-56 | Exhaust/supply fan | Serves AC-14 (Unkai hall) | LCP-3F | DDC-3F-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-56.RUN | Ventilation | EF-56 | Exhaust/supply fan | Serves AC-14 (Unkai hall) | LCP-3F | DDC-3F-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-56.TRIP | Ventilation | EF-56 | Exhaust/supply fan | Serves AC-14 (Unkai hall) | LCP-3F | DDC-3F-03 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-57.SS | Ventilation | EF-57 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-57.RUN | Ventilation | EF-57 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-57.TRIP | Ventilation | EF-57 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-58.SS | Ventilation | EF-58 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-05 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-58.RUN | Ventilation | EF-58 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-58.TRIP | Ventilation | EF-58 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-05 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-59.SS | Ventilation | EF-59 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-05 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-59.RUN | Ventilation | EF-59 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-59.TRIP | Ventilation | EF-59 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-05 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-59-2.SS | Ventilation | EF-59-2 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-05 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-59-2.RUN | Ventilation | EF-59-2 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-59-2.TRIP | Ventilation | EF-59-2 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-05 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-60.SS | Ventilation | EF-60 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-60.RUN | Ventilation | EF-60 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-60.TRIP | Ventilation | EF-60 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-03 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-61.SS | Ventilation | EF-61 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-61.RUN | Ventilation | EF-61 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-61.TRIP | Ventilation | EF-61 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-03 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-62.SS | Ventilation | EF-62 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-62.RUN | Ventilation | EF-62 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-62.TRIP | Ventilation | EF-62 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-67.SS | Ventilation | EF-67 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-06 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-67.RUN | Ventilation | EF-67 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-06 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-67.TRIP | Ventilation | EF-67 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-06 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-69.SS | Ventilation | EF-69 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-69.RUN | Ventilation | EF-69 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-69.TRIP | Ventilation | EF-69 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-70.SS | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-70.RUN | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-70.TRIP | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-70.SPD | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | VFD (INV) speed command | AO | 0-10V | % | Y
EF-70.SPDFB | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-06 |  |  | VFD speed feedback | AI | 4-20mA | %
EF-71.SS | Ventilation | EF-71 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-07 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-71.RUN | Ventilation | EF-71 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-07 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-71.TRIP | Ventilation | EF-71 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-07 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-76.SS | Ventilation | EF-76 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-76.RUN | Ventilation | EF-76 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-76.TRIP | Ventilation | EF-76 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-77.SS | Ventilation | EF-77 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-77.RUN | Ventilation | EF-77 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-77.TRIP | Ventilation | EF-77 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-82.SS | Ventilation | EF-82 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-82.RUN | Ventilation | EF-82 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-82.TRIP | Ventilation | EF-82 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-83.SS | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-83.RUN | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-83.TRIP | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-83.SPD | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | VFD (INV) speed command | AO | 0-10V | % | Y
EF-83.SPDFB | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-3637 | DDC-3637-11 |  |  | VFD speed feedback | AI | 4-20mA | %
EF-84.SS | Ventilation | EF-84 | Exhaust/supply fan | Serves AC-23 (Akasaka kitchen (37F)) | LCP-3637 | DDC-3637-11 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-84.RUN | Ventilation | EF-84 | Exhaust/supply fan | Serves AC-23 (Akasaka kitchen (37F)) | LCP-3637 | DDC-3637-11 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-84.TRIP | Ventilation | EF-84 | Exhaust/supply fan | Serves AC-23 (Akasaka kitchen (37F)) | LCP-3637 | DDC-3637-11 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-85.SS | Ventilation | EF-85 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-3637 | DDC-3637-12 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-85.RUN | Ventilation | EF-85 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-3637 | DDC-3637-12 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-85.TRIP | Ventilation | EF-85 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-3637 | DDC-3637-12 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-86.SS | Ventilation | EF-86 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-3637 | DDC-3637-12 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-86.RUN | Ventilation | EF-86 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-3637 | DDC-3637-12 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-86.TRIP | Ventilation | EF-86 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-3637 | DDC-3637-12 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-89.SS | Ventilation | EF-89 | Exhaust/supply fan | Serves AC-25 (Sirius hall & kitchen) | LCP-3637 | DDC-3637-12 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-89.RUN | Ventilation | EF-89 | Exhaust/supply fan | Serves AC-25 (Sirius hall & kitchen) | LCP-3637 | DDC-3637-12 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-89.TRIP | Ventilation | EF-89 | Exhaust/supply fan | Serves AC-25 (Sirius hall & kitchen) | LCP-3637 | DDC-3637-12 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-97.SS | Ventilation | EF-97 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-HSL | DDC-HSL-14 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-97.RUN | Ventilation | EF-97 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-HSL | DDC-HSL-14 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-97.TRIP | Ventilation | EF-97 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-HSL | DDC-HSL-14 |  |  | Fault | BI | DI dry contact | - |  | Y
EF-98.SS | Ventilation | EF-98 | Exhaust/supply fan | Serves AC-27 (Club Lounge (35F) - 4-pipe) | LCP-3637 | DDC-3637-13 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-98.RUN | Ventilation | EF-98 | Exhaust/supply fan | Serves AC-27 (Club Lounge (35F) - 4-pipe) | LCP-3637 | DDC-3637-13 |  |  | Run status | BI | DI dry contact | - |  |  | Y
EF-98.TRIP | Ventilation | EF-98 | Exhaust/supply fan | Serves AC-27 (Club Lounge (35F) - 4-pipe) | LCP-3637 | DDC-3637-13 |  |  | Fault | BI | DI dry contact | - |  | Y
RF-7.SS | Ventilation | RF-7 | Exhaust/supply fan | Serves AC-3 (B1F guest lift lobby & anteroom) | LCP-HSL | DDC-HSL-14 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
RF-7.RUN | Ventilation | RF-7 | Exhaust/supply fan | Serves AC-3 (B1F guest lift lobby & anteroom) | LCP-HSL | DDC-HSL-14 |  |  | Run status | BI | DI dry contact | - |  |  | Y
RF-7.TRIP | Ventilation | RF-7 | Exhaust/supply fan | Serves AC-3 (B1F guest lift lobby & anteroom) | LCP-HSL | DDC-HSL-14 |  |  | Fault | BI | DI dry contact | - |  | Y
RF-8.SS | Ventilation | RF-8 | Exhaust/supply fan | Serves AC-4 (B1F banquet lobby) | LCP-HSL | DDC-HSL-15 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
RF-8.RUN | Ventilation | RF-8 | Exhaust/supply fan | Serves AC-4 (B1F banquet lobby) | LCP-HSL | DDC-HSL-15 |  |  | Run status | BI | DI dry contact | - |  |  | Y
RF-8.TRIP | Ventilation | RF-8 | Exhaust/supply fan | Serves AC-4 (B1F banquet lobby) | LCP-HSL | DDC-HSL-15 |  |  | Fault | BI | DI dry contact | - |  | Y
RF-9.SS | Ventilation | RF-9 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-HSL | DDC-HSL-15 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
RF-9.RUN | Ventilation | RF-9 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-HSL | DDC-HSL-15 |  |  | Run status | BI | DI dry contact | - |  |  | Y
RF-9.TRIP | Ventilation | RF-9 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-HSL | DDC-HSL-15 |  |  | Fault | BI | DI dry contact | - |  | Y
PAC-1-1.RUN | Packaged units | PAC-1-1 | Packaged AC unit (water-cooled) | 特高電気室 (1) | LCP-PKG | DDC-PKG-01 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PAC-1-1.TRIP | Packaged units | PAC-1-1 | Packaged AC unit (water-cooled) | 特高電気室 (1) | LCP-PKG | DDC-PKG-01 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PAC-1-1.SS | Packaged units | PAC-1-1 | Packaged AC unit (water-cooled) | 特高電気室 (1) | LCP-PKG | DDC-PKG-01 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 24/7 (electrical room)
PAC-1-2.RUN | Packaged units | PAC-1-2 | Packaged AC unit (water-cooled) | 特高電気室 (2) | LCP-PKG | DDC-PKG-01 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PAC-1-2.TRIP | Packaged units | PAC-1-2 | Packaged AC unit (water-cooled) | 特高電気室 (2) | LCP-PKG | DDC-PKG-01 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PAC-1-2.SS | Packaged units | PAC-1-2 | Packaged AC unit (water-cooled) | 特高電気室 (2) | LCP-PKG | DDC-PKG-01 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 24/7 (electrical room)
PAC-2.RUN | Packaged units | PAC-2 | Packaged AC unit (water-cooled) | 第1電気室 / 前室 | LCP-PKG | DDC-PKG-01 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PAC-2.TRIP | Packaged units | PAC-2 | Packaged AC unit (water-cooled) | 第1電気室 / 前室 | LCP-PKG | DDC-PKG-01 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PAC-2.SS | Packaged units | PAC-2 | Packaged AC unit (water-cooled) | 第1電気室 / 前室 | LCP-PKG | DDC-PKG-01 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 24/7 (electrical room)
PAC-3.RUN | Packaged units | PAC-3 | Packaged AC unit (water-cooled) | 第1電気室 (2) | LCP-PKG | DDC-PKG-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PAC-3.TRIP | Packaged units | PAC-3 | Packaged AC unit (water-cooled) | 第1電気室 (2) | LCP-PKG | DDC-PKG-02 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PAC-3.SS | Packaged units | PAC-3 | Packaged AC unit (water-cooled) | 第1電気室 (2) | LCP-PKG | DDC-PKG-02 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 24/7 (electrical room)
PAC-4.RUN | Packaged units | PAC-4 | Packaged AC unit (water-cooled) | 第2電気室 | LCP-PKG | DDC-PKG-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PAC-4.TRIP | Packaged units | PAC-4 | Packaged AC unit (water-cooled) | 第2電気室 | LCP-PKG | DDC-PKG-02 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PAC-4.SS | Packaged units | PAC-4 | Packaged AC unit (water-cooled) | 第2電気室 | LCP-PKG | DDC-PKG-02 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 24/7 (electrical room)
PAC-5.RUN | Packaged units | PAC-5 | Packaged AC unit (water-cooled) | 大宴会場電気室 | LCP-PKG | DDC-PKG-02 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PAC-5.TRIP | Packaged units | PAC-5 | Packaged AC unit (water-cooled) | 大宴会場電気室 | LCP-PKG | DDC-PKG-02 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PAC-5.SS | Packaged units | PAC-5 | Packaged AC unit (water-cooled) | 大宴会場電気室 | LCP-PKG | DDC-PKG-02 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | 24/7 (electrical room)
PCU-1-1.RUN | Packaged units | PCU-1-1 | Packaged AC unit (water-cooled) | ギャラクシー II | LCP-PKG | DDC-PKG-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PCU-1-1.TRIP | Packaged units | PCU-1-1 | Packaged AC unit (water-cooled) | ギャラクシー II | LCP-PKG | DDC-PKG-03 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-1-1.SS | Packaged units | PCU-1-1 | Packaged AC unit (water-cooled) | ギャラクシー II | LCP-PKG | DDC-PKG-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-1-2.RUN | Packaged units | PCU-1-2 | Packaged AC unit (water-cooled) | ギャラクシー I | LCP-PKG | DDC-PKG-03 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PCU-1-2.TRIP | Packaged units | PCU-1-2 | Packaged AC unit (water-cooled) | ギャラクシー I | LCP-PKG | DDC-PKG-03 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-1-2.SS | Packaged units | PCU-1-2 | Packaged AC unit (water-cooled) | ギャラクシー I | LCP-PKG | DDC-PKG-03 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-5.RUN | Packaged units | PCU-5 | Packaged AC unit (water-cooled) | ルミナス | LCP-PKG | DDC-PKG-03 | CP-B1-4 | B1F | Run status | BI | DI dry contact | - |  |  | Y
PCU-5.TRIP | Packaged units | PCU-5 | Packaged AC unit (water-cooled) | ルミナス | LCP-PKG | DDC-PKG-03 | CP-B1-4 | B1F | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-5.SS | Packaged units | PCU-5 | Packaged AC unit (water-cooled) | ルミナス | LCP-PKG | DDC-PKG-03 | CP-B1-4 | B1F | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-6.RUN | Packaged units | PCU-6 | Packaged AC unit (water-cooled) | ギャラクシー III | LCP-PKG | DDC-PKG-04 | CP-B1-4 | B1F | Run status | BI | DI dry contact | - |  |  | Y
PCU-6.TRIP | Packaged units | PCU-6 | Packaged AC unit (water-cooled) | ギャラクシー III | LCP-PKG | DDC-PKG-04 | CP-B1-4 | B1F | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-6.SS | Packaged units | PCU-6 | Packaged AC unit (water-cooled) | ギャラクシー III | LCP-PKG | DDC-PKG-04 | CP-B1-4 | B1F | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-7.RUN | Packaged units | PCU-7 | Packaged AC unit (water-cooled) | グローリー | LCP-PKG | DDC-PKG-04 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PCU-7.TRIP | Packaged units | PCU-7 | Packaged AC unit (water-cooled) | グローリー | LCP-PKG | DDC-PKG-04 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-7.SS | Packaged units | PCU-7 | Packaged AC unit (water-cooled) | グローリー | LCP-PKG | DDC-PKG-04 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-8.RUN | Packaged units | PCU-8 | Packaged AC unit (water-cooled) | オーロラ | LCP-PKG | DDC-PKG-04 | CP-B1-2 | B1F | Run status | BI | DI dry contact | - |  |  | Y
PCU-8.TRIP | Packaged units | PCU-8 | Packaged AC unit (water-cooled) | オーロラ | LCP-PKG | DDC-PKG-04 | CP-B1-2 | B1F | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-8.SS | Packaged units | PCU-8 | Packaged AC unit (water-cooled) | オーロラ | LCP-PKG | DDC-PKG-04 | CP-B1-2 | B1F | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-10.RUN | Packaged units | PCU-10 | Packaged AC unit (water-cooled) | プリズム | LCP-PKG | DDC-PKG-05 | CP-B1-2 | B1F | Run status | BI | DI dry contact | - |  |  | Y
PCU-10.TRIP | Packaged units | PCU-10 | Packaged AC unit (water-cooled) | プリズム | LCP-PKG | DDC-PKG-05 | CP-B1-2 | B1F | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-10.SS | Packaged units | PCU-10 | Packaged AC unit (water-cooled) | プリズム | LCP-PKG | DDC-PKG-05 | CP-B1-2 | B1F | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-11.RUN | Packaged units | PCU-11 | Packaged AC unit (water-cooled) | 客用ELVロビー | LCP-PKG | DDC-PKG-05 | RCP-B1-5 | B1F | Run status | BI | DI dry contact | - |  |  | Y
PCU-11.TRIP | Packaged units | PCU-11 | Packaged AC unit (water-cooled) | 客用ELVロビー | LCP-PKG | DDC-PKG-05 | RCP-B1-5 | B1F | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-11.SS | Packaged units | PCU-11 | Packaged AC unit (water-cooled) | 客用ELVロビー | LCP-PKG | DDC-PKG-05 | RCP-B1-5 | B1F | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-12.RUN | Packaged units | PCU-12 | Packaged AC unit (water-cooled) | 宴会場ロビー (B2F) | LCP-PKG | DDC-PKG-05 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PCU-12.TRIP | Packaged units | PCU-12 | Packaged AC unit (water-cooled) | 宴会場ロビー (B2F) | LCP-PKG | DDC-PKG-05 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-12.SS | Packaged units | PCU-12 | Packaged AC unit (water-cooled) | 宴会場ロビー (B2F) | LCP-PKG | DDC-PKG-05 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PCU-13.RUN | Packaged units | PCU-13 | Packaged AC unit (water-cooled) | 大宴会場前室 | LCP-PKG | DDC-PKG-06 | RCP-B1-5 | B1F | Run status | BI | DI dry contact | - |  |  | Y
PCU-13.TRIP | Packaged units | PCU-13 | Packaged AC unit (water-cooled) | 大宴会場前室 | LCP-PKG | DDC-PKG-06 | RCP-B1-5 | B1F | Fault / alarm | BI | DI dry contact | - |  | Y
PCU-13.SS | Packaged units | PCU-13 | Packaged AC unit (water-cooled) | 大宴会場前室 | LCP-PKG | DDC-PKG-06 | RCP-B1-5 | B1F | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
PMAC-1.RUN | Packaged units | PMAC-1 | Packaged AC unit (water-cooled) | メンテナンスセンター/事務室 | LCP-PKG | DDC-PKG-06 |  |  | Run status | BI | DI dry contact | - |  |  | Y
PMAC-1.TRIP | Packaged units | PMAC-1 | Packaged AC unit (water-cooled) | メンテナンスセンター/事務室 | LCP-PKG | DDC-PKG-06 |  |  | Fault / alarm | BI | DI dry contact | - |  | Y
PMAC-1.SS | Packaged units | PMAC-1 | Packaged AC unit (water-cooled) | メンテナンスセンター/事務室 | LCP-PKG | DDC-PKG-06 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Time/occupancy schedule
REFR-1.ALM1 | Packaged units | REFR-1 | Kitchen refrigeration | B1F 主厨房一括 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — B1F 主厨房一括 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
REFR-1.ALM2 | Packaged units | REFR-1 | Kitchen refrigeration | B1F 厨房冷蔵庫異常一括 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — B1F 厨房冷蔵庫異常一括 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
REFR-1.ALM3 | Packaged units | REFR-1 | Kitchen refrigeration | MR-1 ル・パティオ厨房 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — MR-1 ル・パティオ厨房 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
REFR-1.ALM4 | Packaged units | REFR-1 | Kitchen refrigeration | 2F ゴミ処理室 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — 2F ゴミ処理室 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
REFR-1.ALM5 | Packaged units | REFR-1 | Kitchen refrigeration | 2F カスケイド厨房 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — 2F カスケイド厨房 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
REFR-1.ALM6 | Packaged units | REFR-1 | Kitchen refrigeration | 調理冷蔵庫 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — 調理冷蔵庫 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
REFR-1.ALM7 | Packaged units | REFR-1 | Kitchen refrigeration | 雲海厨房 | LCP-PKG | DDC-PKG-07 |  |  | Cold-store/refrigeration alarm — 雲海厨房 | BI | DI dry contact | - |  | Y |  | 冷蔵庫異常; condenser-water rejected
LTG-AVIATION.CMD | Lighting | LTG-AVIATION | Lighting group | 航空障害灯 (aviation obstruction light) | LCP-LTG | DDC-LTG-01 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-AVIATION.ST | Lighting | LTG-AVIATION | Lighting group | 航空障害灯 (aviation obstruction light) | LCP-LTG | DDC-LTG-01 |  |  | Group status | BI | DI dry contact | -
LTG-NEON.CMD | Lighting | LTG-NEON | Lighting group | ネオンサイン (facade neon sign) | LCP-LTG | DDC-LTG-01 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-NEON.ST | Lighting | LTG-NEON | Lighting group | ネオンサイン (facade neon sign) | LCP-LTG | DDC-LTG-01 |  |  | Group status | BI | DI dry contact | -
LTG-BALCONY-L.CMD | Lighting | LTG-BALCONY-L | Lighting group | バルコニー照明 4~20F | LCP-LTG | DDC-LTG-01 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-BALCONY-L.ST | Lighting | LTG-BALCONY-L | Lighting group | バルコニー照明 4~20F | LCP-LTG | DDC-LTG-01 |  |  | Group status | BI | DI dry contact | -
LTG-BALCONY-H.CMD | Lighting | LTG-BALCONY-H | Lighting group | バルコニー照明 21~37F | LCP-LTG | DDC-LTG-02 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-BALCONY-H.ST | Lighting | LTG-BALCONY-H | Lighting group | バルコニー照明 21~37F | LCP-LTG | DDC-LTG-02 |  |  | Group status | BI | DI dry contact | -
LTG-CORRIDOR.CMD | Lighting | LTG-CORRIDOR | Lighting group | 客用廊下・ELVホール照明 (per-floor batch) | LCP-LTG | DDC-LTG-02 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-CORRIDOR.ST | Lighting | LTG-CORRIDOR | Lighting group | 客用廊下・ELVホール照明 (per-floor batch) | LCP-LTG | DDC-LTG-02 |  |  | Group status | BI | DI dry contact | -
LTG-LOBBY.CMD | Lighting | LTG-LOBBY | Lighting group | 客用ELVロビー・ロビー照明 | LCP-LTG | DDC-LTG-02 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-LOBBY.ST | Lighting | LTG-LOBBY | Lighting group | 客用ELVロビー・ロビー照明 | LCP-LTG | DDC-LTG-02 |  |  | Group status | BI | DI dry contact | -
LTG-SOFFIT.CMD | Lighting | LTG-SOFFIT | Lighting group | 軒天井照明 (1F/2F/3F) | LCP-LTG | DDC-LTG-03 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-SOFFIT.ST | Lighting | LTG-SOFFIT | Lighting group | 軒天井照明 (1F/2F/3F) | LCP-LTG | DDC-LTG-03 |  |  | Group status | BI | DI dry contact | -
LTG-TENANT.CMD | Lighting | LTG-TENANT | Lighting group | テナント間接・ダウンライト | LCP-LTG | DDC-LTG-03 |  |  | On/Off command | BO | DO relay | - | Y |  |  | Time/calendar + astronomical (sunset) schedule
LTG-TENANT.ST | Lighting | LTG-TENANT | Lighting group | テナント間接・ダウンライト | LCP-LTG | DDC-LTG-03 |  |  | Group status | BI | DI dry contact | -
MTR-ELEC-MAIN | Metering | MTR-ELEC-MAIN | Energy meter | Whole building | LCP-DHC | DDC-DHC-06 |  |  | Main electricity (kWh) | AI | Pulse/Modbus | kWh |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-GAS-MAIN | Metering | MTR-GAS-MAIN | Energy meter | Whole building | LCP-DHC | DDC-DHC-06 |  |  | City gas (m³) | AI | Pulse/Modbus | m³ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-WATER-MAIN | Metering | MTR-WATER-MAIN | Energy meter | Whole building | LCP-DHC | DDC-DHC-06 |  |  | City water (m³) | AI | Pulse/Modbus | m³ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-DHC-CHW | Metering | MTR-DHC-CHW | Energy meter | Whole building | LCP-DHC | DDC-DHC-07 |  |  | DHC chilled-water energy (受入) | AI | Pulse/Modbus | GJ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-DHC-STEAM | Metering | MTR-DHC-STEAM | Energy meter | Whole building | LCP-DHC | DDC-DHC-07 |  |  | DHC steam energy (受入) | AI | Pulse/Modbus | t/h |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-DHC-COND | Metering | MTR-DHC-COND | Energy meter | Whole building | LCP-DHC | DDC-DHC-07 |  |  | DHC condensate return (HR) | AI | Pulse/Modbus | L |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-CDW-KWH | Metering | MTR-CDW-KWH | Energy meter | Whole building | LCP-CT | DDC-CT-08 |  |  | Cooling-tower/condenser sub-meter | AI | Pulse/Modbus | kWh |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-AHU-KWH | Metering | MTR-AHU-KWH | Energy meter | Whole building | LCP-HSL | DDC-HSL-17 |  |  | AHU/OAU fans sub-meter | AI | Pulse/Modbus | kWh |  |  | Y | Integrating meter; thermal-demand & peak limiting
POOL-FP.SS | Common | POOL-FP | Pool filtration pump | Pool plant | LCP-HSL | DDC-HSL-16 |  |  | Start/Stop command | BO | DO relay | - | Y |  |  | Time schedule 8:00-19:00
POOL-FP.RUN | Common | POOL-FP | Pool filtration pump | Pool plant | LCP-HSL | DDC-HSL-16 |  |  | Run status | BI | DI dry contact | -
POOL-FP.TRIP | Common | POOL-FP | Pool filtration pump | Pool plant | LCP-HSL | DDC-HSL-16 |  |  | Fault | BI | DI dry contact | - |  | Y

## IO_Summary
System | AI | AO | BI | BO | Total
DHC interface | 11 | 2 | 2 | 2 | 17
Heat source | 92 | 38 | 107 | 35 | 272
Condenser water | 11 | 6 | 38 | 27 | 82
Air side | 143 | 192 | 198 | 53 | 586
Ventilation | 2 | 2 | 72 | 36 | 112
Packaged units | 0 | 0 | 41 | 17 | 58
Lighting | 0 | 0 | 8 | 8 | 16
Metering | 8 | 0 | 0 | 0 | 8
Common | 6 | 0 | 2 | 1 | 9
GRAND TOTAL | 273 | 240 | 468 | 179 | 1160
Devices | 190
Panels | 12
Controllers | 84
Total I/O points | 1160

## Reconciliation
Reconciliation — functional model vs physical panel schedule
This workbook is the drawing-derived FUNCTIONAL model (tagged points + SOO). 판넬별 포인트 정리 26.07.30 is the PHYSICAL panel schedule (per-panel type counts).
Metric | Functional model | Physical schedule (26.07.30)
Scope | tagged points + description + SOO | per-panel type counts (no per-point tags)
Total I/O points | 1160 | 4467
Panels | 12 | 67
Controllers / modules | 84 | 904
Installed capacity (points) | — | 5240
Panels naming equipment served | — | 26
Point types | functional (AI/AO/BI/BO) | physical (DO/DI/BTOT/AI/AO)
Analog input (AI) | 273 | 505
Analog output (AO) | 240 | 86
Binary input (BI ≈ DI) | 468 | 1759
Binary output (BO ≈ DO) | 179 | 1583
Pulse / totalizer (BTOT) | — | 534
Overlap (characterized, purpose known) | 1160 | 1160
Newly surfaced, count-only (tags TBD) | — | 3307
Functional points cross-linked to a physical panel | 431 | 37% of 1160
Note | The physical schedule supplies only per-panel type counts, not individual point tags, so the 3307 count-only points cannot be expanded into fully-described tagged points from that source. The full physical inventory (per panel × type, floor, equipment served) lives in Red5-DHCP-Panels-IO; every physical point is enumerated as a positional tag in the red5-dhcp_commissioning sheets. The 'Phys. panel' / 'Phys. floor' columns on IO_List link the functional AHU/OAU/packaged devices to the physical panel that carries them.

## Points-by-Floor
Physical panels accounting for the full 4,467 points (판넬별 포인트 정리 physical schedule)
The 4,467 installed I/O points live in 67 physical panels (RS/RCP/CP cabinets), grouped here by floor. The 1,160 functional points in this workbook are a drawing-derived subset bucketed into 12 logical LCP panels — see the LCP-to-Physical sheet for how they relate.
Floor / area | Panels | Used points | Capacity
Penthouse (PH) | 9 | 710 | 818
Floor 31 | 1 | 138 | 164
Floor 21 | 1 | 152 | 170
Floor 10 | 1 | 151 | 164
Floor 4 | 7 | 492 | 604
Floor 3 | 5 | 468 | 518
Floor 2 | 6 | 458 | 532
Floor 1 | 5 | 224 | 264
Basement B1 | 11 | 539 | 650
Basement B2 | 16 | 860 | 1012
Basement B3 | 5 | 275 | 344
TOTAL | 67 | 4467 | 5240
Per-panel detail (67 physical panels)
# | Panel | Floor | Equipment served | Used | Cap
1 | RS-PH2-1 | PH2 |  | 66 | 72
2 | RS-PH1-3 | PH1 |  | 165 | 166
3 | CP-PH1-3 | PH1 |  | 13 | 14
4 | CP-R-1 | PH1 |  | 13 | 24
5 | RCP-PH1-3 | PH1 |  | 100 | 118
6 | RCP-PH1-2 | PH1 | AC-24, EVU-11, EVU-13 | 116 | 132
7 | RCP-PH1-1 | PH1 | AC-22, AC-23. EVU-15 | 84 | 116
8 | CP-PH-1 | PH1 |  | 65 | 76
9 | RS-PH1-1 | PH1 |  | 88 | 100
10 | RS-31-1 | 31F |  | 138 | 164
11 | RS-21-1 | 21F |  | 152 | 170
12 | RS-10-1 | 10F |  | 151 | 164
13 | RCP-4-1 | 4F | EVU-8 | 37 | 40
14 | RCP-4-2 | 4F | AC-17, AC-21, EVU-9 | 96 | 114
15 | RCP-4-3 | 4F | AC-20, EVU-10 | 53 | 74
16 | RCP-4-4 | 4F | AC-18, AC-19 | 59 | 74
17 | CP-4-4 | 4F |  | 9 | 20
18 | RS-4-1 | 4F |  | 102 | 110
19 | RS-4-2 | 4F |  | 136 | 172
20 | RCP-3-1 | 3F | AC-14 | 35 | 40
21 | RCP-3-2 | 3F | AC-15, AC-16, EVU-7 | 79 | 98
22 | RS-3-1 | 3F |  | 112 | 128
23 | RS-3-2A | 3F |  | 172 | 182
24 | RS-3-2B | 3F |  | 70 | 70
25 | RCP-2-2 | 2F | AC-11, AC-12, AC-13, EVU-4, EVU-5 | 149 | 170
26 | RCP-2-3 | 2F |  | 64 | 76
27 | RS-2-1 | 2F |  | 23 | 24
28 | RS-2-2 | 2F |  | 102 | 124
29 | RS-2-3 | 2F |  | 96 | 104
30 | EVU-6 | 2F |  | 24 | 34
31 | RCP-1-1 | 1F | EVU-1 | 23 | 26
32 | RCP-1-2 | 1F | AC-7, EVU-2 | 58 | 68
33 | RCP-1-3 | 1F | EVU-3 | 31 | 34
34 | RS-1-1 | 1F |  | 39 | 48
35 | RS-1-2 | 1F |  | 73 | 88
36 | RCP-B1-1 | B1F | AC-5 | 28 | 34
37 | RCP-B1-2 | B1F | AC-2, AC-2 (CO2), AC-6 | 84 | 116
38 | RCP-B1-3 | B1F | AC-4 | 24 | 40
39 | RCP-B1-4 | B1F | AC-2 | 35 | 44
40 | RCP-B1-5 | B1F | PCU-11, PCU-13 | 26 | 28
41 | CP-B1-2 | B1F | PCU-8, PCU-9, PCU-10 | 49 | 58
42 | CP-B1-3 | B1F |  | 0 | 0
43 | CP-B1-4 | B1F | PCU-5, PCU-6, PCU-7-1, PCU-7-2 | 68 | 80
44 | RS-B1-1 | B1F |  | 51 | 56
45 | RS-B1-2 | B1F |  | 114 | 122
46 | RS-B1-3 | B1F |  | 60 | 72
47 | 시스템 제어반 | B2F |  | 25 | 32
48 | RCP-B2-1 | B2F | AC-3 | 29 | 40
49 | RCP-B2-2 | B2F | SF-10, SF-11, EF-10, EF-11 | 31 | 52
50 | RCP-B2-3 | B2F | SF-12, EF-12 | 16 | 26
51 | RCP-B2-4 | B2F |  | 0 | 0
52 | CP-B2-3 | B2F | AC-26 | 28 | 36
53 | CP-B2-4 | B2F |  | 54 | 72
54 | RS-B2-1 | B2F |  | 76 | 92
55 | RS-B2-2 | B2F |  | 78 | 90
56 | RS-B2-3 | B2F |  | 59 | 60
57 | RS-B2-4B | B2F |  | 124 | 128
58 | RS-B2-4A | B2F |  | 31 | 32
59 | RS-B2-5 | B2F |  | 97 | 120
60 | RS-B2-6 | B2F |  | 83 | 92
61 | RS-B2-7 | B2F |  | 129 | 140
62 | P-1 | B2F or B3F (추정) |  | 0 | 0
63 | RCP-B3-1 | B3F | AC-1 | 28 | 40
64 | RCP-B3-2 | B3F | SF-3, EF-2 | 16 | 26
65 | RCP-B3-3 | B3F | SF-4, SF-5, EF-3, EF-4 | 31 | 52
66 | CP-B3-2 | B3F |  | 33 | 54
67 | RS-B3-1 | B3F |  | 167 | 172

## LCP-to-Physical
Logical (LCP) panels → physical panels
Each functional LCP grouping mapped to the physical RS/RCP/CP panel(s) that carry its equipment, via the equipment-served bridge. Plant / DHC / metering / lighting devices are not equipment-tagged in the physical schedule, so those rows show the drawing location + an engineering-judgement hint instead of a hard match.
LCP panel | Drawing location | Points | Matched physical panels (floor) | Linked pts | Coverage | Note (engineering judgement)
BMS-CENTRAL | B2F Central Monitoring Rm | 0 | — | 0 | 0%
LCP-DHC | B2F Machine Room | 56 | — | 0 | 0% | DHC intake devices in B2F machine-room CP-* panels (not equip-tagged)
LCP-CT | Rooftop / PH | 83 | — | 0 | 0% | Tower/condenser devices on rooftop / PH plant panels (not equip-tagged)
LCP-HSL | B2F Machine Room | 222 | CP-B2-3 (B2F), RCP-B1-1 (B1F), RCP-B1-2 (B1F), RCP-B1-3 (B1F), RCP-B2-1 (B2F), RCP-B3-1 (B3F) | 75 | 33% | Low-rise CHW/HW pumps + HX in basement machine-room CP-* panels
LCP-HSH | PH Machine Room | 182 | RCP-PH1-1 (PH1), RCP-PH1-2 (PH1) | 38 | 20% | High-rise + 36/37F pumps/HX incl. R-1 → CP-R-1 (PH1) + basement CP-*
LCP-3637 | 37F PH Machine Room | 171 | RCP-PH1-1 (PH1), RCP-PH1-2 (PH1) | 38 | 22%
LCP-1F | 1F EPS/AHU Room | 54 | RCP-1-1 (1F), RCP-1-2 (1F), RCP-1-3 (1F) | 48 | 88%
LCP-2F | 2F AHU Room | 117 | RCP-2-2 (2F), RCP-B3-2 (B3F) | 63 | 53%
LCP-3F | 3F AHU Room | 68 | RCP-3-1 (3F), RCP-3-2 (3F) | 50 | 73%
LCP-4F | 4F AHU Room | 133 | RCP-4-1 (4F), RCP-4-2 (4F), RCP-4-3 (4F), RCP-4-4 (4F) | 101 | 75%
LCP-PKG | B3F–B1F EPS | 58 | CP-B1-2 (B1F), CP-B1-4 (B1F), RCP-B1-5 (B1F) | 18 | 31% | Packaged units → CP-B1-2 / CP-B1-4 / RCP-B1-5 (PCU tags)
LCP-LTG | Distributed EPS | 16 | — | 0 | 0% | Common-area/facade lighting distributed across RS-* room panels
How to read this | The 'Matched physical panels' column is a BEST-EFFORT bridge: a functional device (e.g. AC-17) is linked to a physical panel only when that panel's 'equipment served' column names the same tag. So coverage is high for the air-side floor LCPs (AHUs/OAUs) and partial elsewhere. Rows at 0% coverage (BMS-CENTRAL, LCP-DHC, LCP-CT, LCP-LTG) hold plant / DHC / metering / lighting points that are NOT equipment-tagged in the physical schedule — use the drawing location + judgement note for those. Caveat: matching is by tag string only, so a repeated fan/unit number can produce a cross-floor coincidence (e.g. a 2F SF tag also appearing on a basement fan panel) — verify against the drawings before relying on a single-panel assignment.

## Delta-Controllers
Delta controllers & I/O modules — type tally + all 4,467 points grouped by panel
The physical schedule lists, per panel, the Delta 'controller & I/O module' fleet that carries its points. Below: the type tally (unit counts) and every panel's controller composition with its used-point total, so the full 4,467 points roll up to the 904 units.
Controller / module type | Role | Units | Share of fleet
Red5-PLUS-ROOM | Room controller (BACnet, onboard I/O) | 90 | 10.0%
CON-T1L | Network/BACnet controller | 80 | 8.8%
Red5-EXPAND-04 | Bus expander (hosts I/O modules) | 100 | 11.1%
Red5-MODULE-4F4xP | I/O module | 422 | 46.7%
Red5-MODULE-8xP | I/O module | 127 | 14.0%
Red5-MODULE-8PxP | I/O module | 85 | 9.4%
TOTAL |  | 904 | 100%
Rollup
Controllers (ROOM + CON-T1L) | 170
Bus expanders (EXPAND-04) | 100
I/O modules (4F4xP + 8xP + 8PxP) | 634
Total controllers + modules | 904
Used I/O points | 4467
Installed point capacity | 5240
Fleet point utilisation | 85%
Per-panel controller composition (all 4,467 points grouped to each panel's fleet)
# | Panel | Floor | ROOM | CON-T1L | EXPAND-04 | 4F4xP | 8xP | 8PxP | Modules | Used pts | Cap
1 | RS-PH2-1 | PH2 | 1 | 1 | 2 | 0 | 6 | 3 | 13 | 66 | 72
2 | RS-PH1-3 | PH1 | 2 | 1 | 4 | 11 | 6 | 4 | 28 | 165 | 166
3 | CP-PH1-3 | PH1 | 1 | 1 | 0 | 0 | 2 | 1 | 5 | 13 | 14
4 | CP-R-1 | PH1 | 1 | 1 | 0 | 2 | 0 | 0 | 4 | 13 | 24
5 | RCP-PH1-3 | PH1 | 2 | 1 | 2 | 15 | 0 | 0 | 20 | 100 | 118
6 | RCP-PH1-2 | PH1 | 2 | 1 | 2 | 16 | 0 | 0 | 21 | 116 | 132
7 | RCP-PH1-1 | PH1 | 2 | 1 | 2 | 12 | 0 | 1 | 18 | 84 | 116
8 | CP-PH-1 | PH1 | 1 | 1 | 2 | 4 | 5 | 0 | 13 | 65 | 76
9 | RS-PH1-1 | PH1 | 1 | 1 | 2 | 4 | 6 | 2 | 16 | 88 | 100
10 | RS-31-1 | 31F | 2 | 1 | 3 | 16 | 0 | 2 | 24 | 138 | 164
11 | RS-21-1 | 21F | 2 | 1 | 4 | 16 | 3 | 2 | 28 | 152 | 170
12 | RS-10-1 | 10F | 2 | 1 | 3 | 17 | 2 | 1 | 26 | 151 | 164
13 | RCP-4-1 | 4F | 1 | 1 | 1 | 5 | 0 | 1 | 9 | 37 | 40
14 | RCP-4-2 | 4F | 2 | 1 | 2 | 12 | 0 | 2 | 19 | 96 | 114
15 | RCP-4-3 | 4F | 1 | 1 | 1 | 7 | 0 | 1 | 11 | 53 | 74
16 | RCP-4-4 | 4F | 1 | 1 | 2 | 8 | 0 | 1 | 13 | 59 | 74
17 | CP-4-4 | 4F | 1 | 1 | 0 | 1 | 1 | 0 | 4 | 9 | 20
18 | RS-4-1 | 4F | 2 | 1 | 2 | 7 | 2 | 4 | 18 | 102 | 110
19 | RS-4-2 | 4F | 2 | 1 | 3 | 12 | 2 | 4 | 24 | 136 | 172
20 | RCP-3-1 | 3F | 1 | 1 | 1 | 4 | 0 | 1 | 8 | 35 | 40
21 | RCP-3-2 | 3F | 1 | 1 | 2 | 9 | 1 | 1 | 15 | 79 | 98
22 | RS-3-1 | 3F | 2 | 1 | 2 | 7 | 7 | 1 | 20 | 112 | 128
23 | RS-3-2A | 3F | 2 | 1 | 4 | 13 | 4 | 6 | 30 | 172 | 182
24 | RS-3-2B | 3F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 70
25 | RCP-2-2 | 2F | 2 | 1 | 4 | 22 | 0 | 0 | 29 | 149 | 170
26 | RCP-2-3 | 2F | 1 | 1 | 2 | 8 | 0 | 1 | 13 | 64 | 76
27 | RS-2-1 | 2F | 1 | 1 | 0 | 0 | 1 | 2 | 5 | 23 | 24
28 | RS-2-2 | 2F | 2 | 1 | 2 | 7 | 2 | 4 | 18 | 102 | 124
29 | RS-2-3 | 2F | 2 | 1 | 2 | 8 | 1 | 4 | 18 | 96 | 104
30 | EVU-6 | 2F | 1 | 1 | 0 | 3 | 1 | 0 | 6 | 24 | 34
31 | RCP-1-1 | 1F | 1 | 1 | 0 | 3 | 0 | 0 | 5 | 23 | 26
32 | RCP-1-2 | 1F | 1 | 1 | 2 | 8 | 0 | 1 | 13 | 58 | 68
33 | RCP-1-3 | 1F | 1 | 1 | 1 | 5 | 0 | 0 | 8 | 31 | 34
34 | RS-1-1 | 1F | 1 | 1 | 1 | 4 | 1 | 1 | 9 | 39 | 48
35 | RS-1-2 | 1F | 1 | 1 | 2 | 7 | 1 | 2 | 14 | 73 | 88
36 | RCP-B1-1 | B1F | 1 | 1 | 1 | 3 | 1 | 1 | 8 | 28 | 34
37 | RCP-B1-2 | B1F | 1 | 1 | 2 | 10 | 1 | 1 | 16 | 84 | 116
38 | RCP-B1-3 | B1F | 1 | 1 | 1 | 4 | 0 | 1 | 8 | 24 | 40
39 | RCP-B1-4 | B1F | 1 | 1 | 1 | 4 | 1 | 0 | 8 | 35 | 44
40 | RCP-B1-5 | B1F | 1 | 1 | 0 | 4 | 0 | 0 | 6 | 26 | 28
41 | CP-B1-2 | B1F | 1 | 1 | 2 | 9 | 0 | 0 | 13 | 49 | 58
42 | CP-B1-3 | B1F | 1 | 1 | 0 | 4 | 0 | 0 | 6 | 0 | 0
43 | CP-B1-4 | B1F | 1 | 1 | 2 | 12 | 0 | 0 | 16 | 68 | 80
44 | RS-B1-1 | B1F | 1 | 1 | 1 | 3 | 1 | 3 | 10 | 51 | 56
45 | RS-B1-2 | B1F | 2 | 1 | 2 | 10 | 3 | 2 | 20 | 114 | 122
46 | RS-B1-3 | B1F | 1 | 1 | 1 | 5 | 2 | 1 | 11 | 60 | 72
47 | 시스템 제어반 | B2F | 6 | 16 | 0 | 0 | 4 | 0 | 26 | 25 | 32
48 | RCP-B2-1 | B2F | 1 | 1 | 1 | 4 | 0 | 1 | 8 | 29 | 40
49 | RCP-B2-2 | B2F | 1 | 1 | 1 | 3 | 1 | 1 | 8 | 31 | 52
50 | RCP-B2-3 | B2F | 1 | 1 | 0 | 2 | 1 | 1 | 6 | 16 | 26
51 | RCP-B2-4 | B2F | 1 | 1 | 0 | 4 | 0 | 0 | 6 | 0 | 0
52 | CP-B2-3 | B2F | 1 | 1 | 1 | 6 | 0 | 0 | 9 | 28 | 36
53 | CP-B2-4 | B2F | 1 | 1 | 1 | 3 | 4 | 0 | 10 | 54 | 72
54 | RS-B2-1 | B2F | 1 | 1 | 2 | 6 | 4 | 1 | 15 | 76 | 92
55 | RS-B2-2 | B2F | 1 | 1 | 2 | 7 | 3 | 1 | 15 | 78 | 90
56 | RS-B2-3 | B2F | 1 | 1 | 1 | 4 | 3 | 1 | 11 | 59 | 60
57 | RS-B2-4B | B2F | 2 | 1 | 2 | 4 | 11 | 1 | 21 | 124 | 128
58 | RS-B2-4A | B2F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 32
59 | RS-B2-5 | B2F | 2 | 1 | 2 | 3 | 6 | 5 | 19 | 97 | 120
60 | RS-B2-6 | B2F | 1 | 1 | 2 | 4 | 4 | 3 | 15 | 83 | 92
61 | RS-B2-7 | B2F | 2 | 1 | 3 | 11 | 4 | 2 | 23 | 129 | 140
62 | P-1 | B2F or B3F (추정) | 1 | 1 | 0 | 4 | 0 | 0 | 6 | 0 | 0
63 | RCP-B3-1 | B3F | 1 | 1 | 1 | 4 | 0 | 1 | 8 | 28 | 40
64 | RCP-B3-2 | B3F | 1 | 1 | 0 | 2 | 1 | 1 | 6 | 16 | 26
65 | RCP-B3-3 | B3F | 1 | 1 | 1 | 3 | 1 | 1 | 8 | 31 | 52
66 | CP-B3-2 | B3F | 1 | 1 | 1 | 1 | 3 | 1 | 8 | 33 | 54
67 | RS-B3-1 | B3F | 2 | 1 | 4 | 6 | 14 | 2 | 29 | 167 | 172
| TOTAL |  | 90 | 80 | 100 | 422 | 127 | 85 | 904 | 4467 | 5240
Note | The physical schedule tallies points at the panel level and controllers/modules by type; it does not assign each point to a specific module. Points are therefore grouped to the panel's whole controller fleet (Used pts vs installed capacity), and the type tally above gives the controller-type counts. Naming: Red5-PLUS-ROOM & CON-T1L are controllers; Red5-EXPAND-04 is a bus expander; Red5-MODULE-4F4xP/8xP/8PxP are I/O point modules.

## Legend
Abbreviation | Meaning
AI | Analog Input (sensor: temperature, humidity, pressure, flow, power, position fb)
AO | Analog Output (modulating command: valve %, damper %, VFD speed %)
BI | Binary Input (status / fault / proof dry contact)
BO | Binary Output (start/stop / open-close relay)
SP/Sched | Point carries a setpoint or time/seasonal/event schedule
CHW / CW | Chilled water / Condenser water
SAT / RAT | Supply-air temp / Return-air temp
CCV / HCV | Cooling-coil valve / Heating-coil (steam) valve
INV | Inverter / VFD fan speed control
Zero-energy band | Deadband between heating & cooling to prevent simultaneous operation
DHC | District Heating & Cooling (external steam / chilled supply) — PRIMARY source
HEX / EX | Plate heat exchanger (HEX-1 DHC tie-in; EX-2 laundry, EX-3 kitchen, EX4 36/37F buffer)
EX-1 | Winter free-cooling heat exchanger (冬期用熱交換器)
CS / CR | DHC chilled supply / return header
SS / HR | DHC steam supply / hot (condensate) return; 8k=0.8 MPa, 2k=0.2 MPa
R-1 | Local 36/37F water-cooled SCREW chiller — Ebara RHS DW202M2 (370 kW, COP 4.5, twin screw, R-407C), DHC-backup
CDP | Condenser-water pump (cooling-tower loop)
CP / HP | Chilled-water pump / hot-water (heating-loop) pump
CT | Cooling tower (INV fan cell + basin common points)
HWT-1 | Hot-well / condensate tank
PCU/PAC/PMAC | Packaged (water-cooled) air-conditioners — status/alarm on BMS
OAU (EVU) | Outdoor-air / make-up-air unit
順序 / 群起動 | Duty sequence / group-start staging of like pumps