## Cover
Red5-DHCP — BMS I/O List & Panel / Controller Schedule
ANA InterContinental Tokyo — District Heating & Cooling (DHC) connected hotel BMS
Building | SRC, B3–37F, ~98,331 m²; Azbil (savic-net) BMS
Energy source | District Heating & Cooling: DHC chilled-water intake (冷水受入, low+high) via HEX-1 + DHC steam (蒸気受入, low @B2F / high @rooftop). Local chillers are BACKUP (順序切替).
Local plant | RC-1 chillers ×3 (370 kW, COP 4.51, DHC backup), CP-8 primary CHW pumps ×3, CP-7 secondary distribution, HEX-1 plate HX (395 kW), CT-1/CT-2 (2 INV fans each), condenser pumps
Air side | AC-1..27 AHUs (public/kitchen), EVU-1..15 outdoor-air units, guest-room FCU zone-groups (5-20F & 20-35F N/S/SE/SW, 4-pipe on DHC water), EF/SF/RF fans
ESCO control scope | Pump optimization, outdoor-air-unit optimization, thermal-demand control (per 共-01 spec)
BMS platform | Azbil savic-netFX2 (savic-net FX2), S/W 機能仕様 dated 2015/04/09 — confirmed from the 144-page Azbil 納入仕様書 (software function spec, not an equipment list)
Sheets | Panels · Controllers · IO_List · IO_Summary · Legend
Basis | As-built M-01 equipment schedule, 共-01 ESCO spec, 空調機スケジュール_20251127.xlsx, Azbil savic-netFX2 S/W 納入仕様書 (platform + supervisory functions)
Note | Items marked 'INFERRED' (secondary/HW pumps, FCU quantity) must be confirmed against the M-01 mechanical equipment schedule in the as-built set — they are NOT in the Azbil 納入仕様書 (that is the savic-netFX2 software function spec).

## Panels
Panel ID | Description | Location | Areas / Systems served | Controllers | I/O points
BMS-CENTRAL | Azbil savic-netFX2 central monitoring (中央監視) | B2F Central Monitoring Rm | Whole-building supervisory on savic-netFX2 (S/W spec 2015/04/09): point mgmt, start-stop/setpoint operation, status & alarm/event processing, time-program + calendar + event-program control, seasonal changeover (batch), remote-setpoint schedules, runtime/start-count & deviation/hi-lo limit monitoring, trend + periodic data collection, daily/monthly reports, energy CSV export, numeric/logic operations, power-failure/restoration handling, user/access mgmt, maintenance & spare-parts mgmt | 0 | 0
LCP-PH | Heat-source & high-rise field panel | PH Machine Room | Chillers, primary/condenser pumps, cooling towers, HEX-1, high-rise DHC steam, PH/high-rise AHUs & OAUs | 20 | 324
LCP-B2 | Low-rise heat-interface & basement panel | B2F Machine Room | Low-rise DHC steam interface, secondary/hot-water pumps, pool filtration, basement AHUs, main meters | 12 | 138
LCP-1F | 1F–2F air-side panel | 1F EPS/AHU Room | AC-7, EVU-1..3 (1F ceremony/banquet/lobby) | 3 | 54
LCP-2F | 2F air-side panel | 2F AHU Room | AC-8..13, EVU-4..6 (atrium, Prominence, offices/tenants) | 4 | 117
LCP-3F | 3F air-side panel | 3F AHU Room | AC-14..16, EVU-7 (Unkai/Karin/DaVinci, chapel) | 4 | 68
LCP-4F | 4F–5F air-side panel | 4F AHU Room | AC-17..21, EVU-8..10 (kitchens, low-rise guest-room OAUs) | 9 | 161

## Controllers
Controller ID | Panel | Type | Devices served | Point count
DDC-PH-01 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | RC-1-1, RC-1-2, RC-1-3 | 30
DDC-PH-02 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | CP-8-1, CP-8-2, CP-8-3 | 21
DDC-PH-03 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | CWP-1, CWP-2, CWP-3 | 15
DDC-PH-04 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | CT-1-1, CT-1-2, CT-2-1 | 24
DDC-PH-05 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | CT-2-2 | 8
DDC-PH-06 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | HEX-1 | 7
DDC-PH-07 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | CP-7-1, CP-7-2 | 14
DDC-PH-08 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | DHC-CHW-H | 9
DDC-PH-09 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | DHC-STEAM-H | 7
DDC-PH-10 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | AC-22, AC-23, AC-24 | 38
DDC-PH-11 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | AC-25, AC-27 | 26
DDC-PH-12 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | EVU-11, EVU-12, EVU-13 | 39
DDC-PH-13 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | EVU-14, EVU-15 | 24
DDC-PH-14 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | FCU-H-N, FCU-H-S, FCU-H-SE | 21
DDC-PH-15 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | FCU-H-SW, FCU-3637 | 14
DDC-PH-16 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | EF-82, EF-83, EF-84 | 11
DDC-PH-17 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | EF-85, EF-86, EF-89 | 9
DDC-PH-18 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | EF-98 | 3
DDC-PH-19 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | OA-STN | 2
DDC-PH-20 | LCP-PH | DDC field controller (Azbil Infilex/savic-net class) | MTR-DHC-STEAM-H, MTR-CHILLER-KWH | 2
DDC-B2-01 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | HWP-1, HWP-2 | 14
DDC-B2-02 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | DHC-CHW-L | 9
DDC-B2-03 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | DHC-STEAM-L | 7
DDC-B2-04 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | AC-1, AC-2, AC-3 | 29
DDC-B2-05 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | AC-4, AC-5, AC-6 | 34
DDC-B2-06 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | AC-26 | 12
DDC-B2-07 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | SF-6, EF-28, EF-32 | 9
DDC-B2-08 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | EF-33, EF-97, RF-7 | 9
DDC-B2-09 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | RF-8, RF-9 | 6
DDC-B2-10 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | POOL-FP | 3
DDC-B2-11 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | MTR-ELEC-MAIN, MTR-GAS-MAIN, MTR-WATER-MAIN | 3
DDC-B2-12 | LCP-B2 | DDC field controller (Azbil Infilex/savic-net class) | MTR-DHC-STEAM-L, MTR-DHC-CHW, MTR-AHU-KWH | 3
DDC-1F-01 | LCP-1F | DDC field controller (Azbil Infilex/savic-net class) | AC-7 | 12
DDC-1F-02 | LCP-1F | DDC field controller (Azbil Infilex/savic-net class) | EVU-1, EVU-2, EVU-3 | 36
DDC-1F-03 | LCP-1F | DDC field controller (Azbil Infilex/savic-net class) | EF-41, EF-42 | 6
DDC-2F-01 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | AC-8, AC-9, AC-10 | 36
DDC-2F-02 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | AC-11, AC-12, AC-13 | 36
DDC-2F-03 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | EVU-4, EVU-5, EVU-6 | 36
DDC-2F-04 | LCP-2F | DDC field controller (Azbil Infilex/savic-net class) | EF-2-1, EF-46, EF-47 | 9
DDC-3F-01 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | AC-14, AC-15, AC-16 | 38
DDC-3F-02 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | EVU-7 | 12
DDC-3F-03 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | EF-56, EF-60, EF-61 | 9
DDC-3F-04 | LCP-3F | DDC field controller (Azbil Infilex/savic-net class) | EF-62, EF-76, EF-77 | 9
DDC-4F-01 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | AC-17, AC-18, AC-19 | 38
DDC-4F-02 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | AC-20, AC-21 | 24
DDC-4F-03 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EVU-8, EVU-9, EVU-10 | 39
DDC-4F-04 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | FCU-L-N, FCU-L-S, FCU-L-SE | 21
DDC-4F-05 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | FCU-L-SW | 7
DDC-4F-06 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-54, EF-55, EF-57 | 9
DDC-4F-07 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-58, EF-59, EF-59-2 | 9
DDC-4F-08 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-67, EF-69, EF-70 | 11
DDC-4F-09 | LCP-4F | DDC field controller (Azbil Infilex/savic-net class) | EF-71 | 3

## IO_List
Point Tag | System | Device ID | Device Type | Area / Served | Panel | Controller | Point Description | I/O Type | Signal / Range | Units | SP/Sched | Alarm | Trend | Notes / Basis
RC-1-1.RUN | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Run status | BI | DI dry contact | - |  |  | Y
RC-1-1.TRIP | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Common fault / trip | BI | DI dry contact | - |  | Y
RC-1-1.LR | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Local/Remote status | BI | DI dry contact | -
RC-1-1.SS | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Start/Stop command | BO | DO relay | - | Y |  |  | BACKUP to DHC chilled water; lead/lag staged; source seq 順序切替
RC-1-1.DMD | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Capacity/demand limit | AO | 0-10V | % | Y |  |  | Demand-limit / soft-load
RC-1-1.CHWST | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | CHW supply (leaving) temp | AI | 4-20mA | °C |  | Y | Y | Design 7°C
RC-1-1.CHWRT | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | CHW return (entering) temp | AI | 4-20mA | °C |  |  | Y | Design 12°C
RC-1-1.CWRT | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Condenser water leaving temp | AI | 4-20mA | °C |  |  | Y
RC-1-1.KW | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Electrical input power | AI | 4-20mA | kW |  |  | Y | For COP / kW-per-ton
RC-1-1.FLW | Heat source | RC-1-1 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Evaporator flow proof | BI | DI dry contact | - |  | Y
RC-1-2.RUN | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Run status | BI | DI dry contact | - |  |  | Y
RC-1-2.TRIP | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Common fault / trip | BI | DI dry contact | - |  | Y
RC-1-2.LR | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Local/Remote status | BI | DI dry contact | -
RC-1-2.SS | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Start/Stop command | BO | DO relay | - | Y |  |  | BACKUP to DHC chilled water; lead/lag staged; source seq 順序切替
RC-1-2.DMD | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Capacity/demand limit | AO | 0-10V | % | Y |  |  | Demand-limit / soft-load
RC-1-2.CHWST | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | CHW supply (leaving) temp | AI | 4-20mA | °C |  | Y | Y | Design 7°C
RC-1-2.CHWRT | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | CHW return (entering) temp | AI | 4-20mA | °C |  |  | Y | Design 12°C
RC-1-2.CWRT | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Condenser water leaving temp | AI | 4-20mA | °C |  |  | Y
RC-1-2.KW | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Electrical input power | AI | 4-20mA | kW |  |  | Y | For COP / kW-per-ton
RC-1-2.FLW | Heat source | RC-1-2 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Evaporator flow proof | BI | DI dry contact | - |  | Y
RC-1-3.RUN | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Run status | BI | DI dry contact | - |  |  | Y
RC-1-3.TRIP | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Common fault / trip | BI | DI dry contact | - |  | Y
RC-1-3.LR | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Local/Remote status | BI | DI dry contact | -
RC-1-3.SS | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Start/Stop command | BO | DO relay | - | Y |  |  | BACKUP to DHC chilled water; lead/lag staged; source seq 順序切替
RC-1-3.DMD | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Capacity/demand limit | AO | 0-10V | % | Y |  |  | Demand-limit / soft-load
RC-1-3.CHWST | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | CHW supply (leaving) temp | AI | 4-20mA | °C |  | Y | Y | Design 7°C
RC-1-3.CHWRT | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | CHW return (entering) temp | AI | 4-20mA | °C |  |  | Y | Design 12°C
RC-1-3.CWRT | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Condenser water leaving temp | AI | 4-20mA | °C |  |  | Y
RC-1-3.KW | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Electrical input power | AI | 4-20mA | kW |  |  | Y | For COP / kW-per-ton
RC-1-3.FLW | Heat source | RC-1-3 | Water-cooled chiller | PH machine room | LCP-PH | DDC-PH-01 | Evaporator flow proof | BI | DI dry contact | - |  | Y
CP-8-1.RUN | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Run status | BI | DI dry contact | - |  |  | Y
CP-8-1.TRIP | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-8-1.SS | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Start/Stop command | BO | DO relay | -
CP-8-1.SPD | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD speed command | AO | 0-10V | % | Y |  |  | Interlock w/ chiller; VFD
CP-8-1.SPDFB | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-8-1.KW | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Power | AI | 4-20mA | kW |  |  | Y
CP-8-1.FLW | Heat source | CP-8-1 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-8-2.RUN | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Run status | BI | DI dry contact | - |  |  | Y
CP-8-2.TRIP | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-8-2.SS | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Start/Stop command | BO | DO relay | -
CP-8-2.SPD | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD speed command | AO | 0-10V | % | Y |  |  | Interlock w/ chiller; VFD
CP-8-2.SPDFB | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-8-2.KW | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Power | AI | 4-20mA | kW |  |  | Y
CP-8-2.FLW | Heat source | CP-8-2 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-8-3.RUN | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Run status | BI | DI dry contact | - |  |  | Y
CP-8-3.TRIP | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-8-3.SS | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Start/Stop command | BO | DO relay | -
CP-8-3.SPD | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD speed command | AO | 0-10V | % | Y |  |  | Interlock w/ chiller; VFD
CP-8-3.SPDFB | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-8-3.KW | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Power | AI | 4-20mA | kW |  |  | Y
CP-8-3.FLW | Heat source | CP-8-3 | Primary CHW pump | PH machine room | LCP-PH | DDC-PH-02 | Flow/DP proof | BI | DI dry contact | - |  | Y
CWP-1.RUN | Heat source | CWP-1 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Run status | BI | DI dry contact | - |  |  | Y
CWP-1.TRIP | Heat source | CWP-1 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Fault | BI | DI dry contact | - |  | Y
CWP-1.SS | Heat source | CWP-1 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Start/Stop command | BO | DO relay | - |  |  |  | Interlock w/ chiller
CWP-1.KW | Heat source | CWP-1 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Power | AI | 4-20mA | kW |  |  | Y
CWP-1.FLW | Heat source | CWP-1 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Flow/DP proof | BI | DI dry contact | - |  | Y
CWP-2.RUN | Heat source | CWP-2 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Run status | BI | DI dry contact | - |  |  | Y
CWP-2.TRIP | Heat source | CWP-2 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Fault | BI | DI dry contact | - |  | Y
CWP-2.SS | Heat source | CWP-2 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Start/Stop command | BO | DO relay | - |  |  |  | Interlock w/ chiller
CWP-2.KW | Heat source | CWP-2 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Power | AI | 4-20mA | kW |  |  | Y
CWP-2.FLW | Heat source | CWP-2 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Flow/DP proof | BI | DI dry contact | - |  | Y
CWP-3.RUN | Heat source | CWP-3 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Run status | BI | DI dry contact | - |  |  | Y
CWP-3.TRIP | Heat source | CWP-3 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Fault | BI | DI dry contact | - |  | Y
CWP-3.SS | Heat source | CWP-3 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Start/Stop command | BO | DO relay | - |  |  |  | Interlock w/ chiller
CWP-3.KW | Heat source | CWP-3 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Power | AI | 4-20mA | kW |  |  | Y
CWP-3.FLW | Heat source | CWP-3 | Condenser-water pump | PH / outdoor | LCP-PH | DDC-PH-03 | Flow/DP proof | BI | DI dry contact | - |  | Y
CT-1-1.RUN | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan run status | BI | DI dry contact | - |  |  | Y
CT-1-1.TRIP | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan fault | BI | DI dry contact | - |  | Y
CT-1-1.SS | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan start/stop | BO | DO relay | -
CT-1-1.SPD | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-1-1.SPDFB | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-1-1.LVL | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Basin water level | AI | 4-20mA | % |  | Y
CT-1-1.MU | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Make-up water valve | BO | DO relay | -
CT-1-1.BLD | Heat source | CT-1-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Bleed/blowdown valve | BO | DO relay | -
CT-1-2.RUN | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan run status | BI | DI dry contact | - |  |  | Y
CT-1-2.TRIP | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan fault | BI | DI dry contact | - |  | Y
CT-1-2.SS | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan start/stop | BO | DO relay | -
CT-1-2.SPD | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-1-2.SPDFB | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-1-2.LVL | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Basin water level | AI | 4-20mA | % |  | Y
CT-1-2.MU | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Make-up water valve | BO | DO relay | -
CT-1-2.BLD | Heat source | CT-1-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Bleed/blowdown valve | BO | DO relay | -
CT-2-1.RUN | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan run status | BI | DI dry contact | - |  |  | Y
CT-2-1.TRIP | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan fault | BI | DI dry contact | - |  | Y
CT-2-1.SS | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan start/stop | BO | DO relay | -
CT-2-1.SPD | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-2-1.SPDFB | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-2-1.LVL | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Basin water level | AI | 4-20mA | % |  | Y
CT-2-1.MU | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Make-up water valve | BO | DO relay | -
CT-2-1.BLD | Heat source | CT-2-1 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-04 | Bleed/blowdown valve | BO | DO relay | -
CT-2-2.RUN | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Fan run status | BI | DI dry contact | - |  |  | Y
CT-2-2.TRIP | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Fan fault | BI | DI dry contact | - |  | Y
CT-2-2.SS | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Fan start/stop | BO | DO relay | -
CT-2-2.SPD | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Fan VFD speed command | AO | 0-10V | % | Y |  |  | Wet-bulb + approach reset
CT-2-2.SPDFB | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Fan speed feedback | AI | 4-20mA | % |  |  | Y
CT-2-2.LVL | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Basin water level | AI | 4-20mA | % |  | Y
CT-2-2.MU | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Make-up water valve | BO | DO relay | -
CT-2-2.BLD | Heat source | CT-2-2 | Cooling tower cell | Rooftop | LCP-PH | DDC-PH-05 | Bleed/blowdown valve | BO | DO relay | -
HEX-1.P-IN | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Primary inlet temp | AI | 4-20mA | °C |  |  | Y | Design 7°C
HEX-1.P-OUT | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Primary outlet temp | AI | 4-20mA | °C |  |  | Y | Design 12°C
HEX-1.S-IN | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Secondary inlet temp | AI | 4-20mA | °C |  |  | Y | Design 15°C
HEX-1.S-OUT | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Secondary outlet (supply) temp | AI | 4-20mA | °C | Y | Y | Y | Design 10°C; reset in mild wx
HEX-1.S-FLW | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Secondary supply flow | AI | 4-20mA | L/min |  |  | Y
HEX-1.PV | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Primary control valve | AO | 0-10V | % | Y |  |  | Modulate to hold S-OUT
HEX-1.PVFB | Heat source | HEX-1 | Plate heat exchanger | Outdoor / PH | LCP-PH | DDC-PH-06 | Primary valve position fb | AI | 4-20mA | %
CP-7-1.RUN | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Run status | BI | DI dry contact | - |  |  | Y
CP-7-1.TRIP | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-7-1.SS | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Start/Stop command | BO | DO relay | -
CP-7-1.SPD | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | VFD speed command | AO | 0-10V | % | Y |  |  | CP-7 secondary loop; DP-reset from most-open valve (qty per as-built)
CP-7-1.SPDFB | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-7-1.KW | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Power | AI | 4-20mA | kW |  |  | Y
CP-7-1.FLW | Heat source | CP-7-1 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Flow/DP proof | BI | DI dry contact | - |  | Y
CP-7-2.RUN | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Run status | BI | DI dry contact | - |  |  | Y
CP-7-2.TRIP | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | VFD/pump fault | BI | DI dry contact | - |  | Y
CP-7-2.SS | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Start/Stop command | BO | DO relay | -
CP-7-2.SPD | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | VFD speed command | AO | 0-10V | % | Y |  |  | CP-7 secondary loop; DP-reset from most-open valve (qty per as-built)
CP-7-2.SPDFB | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
CP-7-2.KW | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Power | AI | 4-20mA | kW |  |  | Y
CP-7-2.FLW | Heat source | CP-7-2 | Secondary CHW distribution pump | PH machine room | LCP-PH | DDC-PH-07 | Flow/DP proof | BI | DI dry contact | - |  | Y
HWP-1.RUN | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Run status | BI | DI dry contact | - |  |  | Y
HWP-1.TRIP | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | VFD/pump fault | BI | DI dry contact | - |  | Y
HWP-1.SS | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Start/Stop command | BO | DO relay | -
HWP-1.SPD | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | VFD speed command | AO | 0-10V | % | Y |  |  | INFERRED; serves 4-pipe FCU/coil heating
HWP-1.SPDFB | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HWP-1.KW | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Power | AI | 4-20mA | kW |  |  | Y
HWP-1.FLW | Heat source | HWP-1 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Flow/DP proof | BI | DI dry contact | - |  | Y
HWP-2.RUN | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Run status | BI | DI dry contact | - |  |  | Y
HWP-2.TRIP | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | VFD/pump fault | BI | DI dry contact | - |  | Y
HWP-2.SS | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Start/Stop command | BO | DO relay | -
HWP-2.SPD | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | VFD speed command | AO | 0-10V | % | Y |  |  | INFERRED; serves 4-pipe FCU/coil heating
HWP-2.SPDFB | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | VFD speed feedback | AI | 4-20mA | % |  |  | Y
HWP-2.KW | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Power | AI | 4-20mA | kW |  |  | Y
HWP-2.FLW | Heat source | HWP-2 | Hot-water pump (steam-HEX loop) | B2F machine room | LCP-B2 | DDC-B2-01 | Flow/DP proof | BI | DI dry contact | - |  | Y
DHC-CHW-L.ST | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Intake (supply header) temp | AI | 4-20mA | °C |  | Y | Y | DHC冷水受入ヘッダ ~7°C
DHC-CHW-L.RT | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Return header temp | AI | 4-20mA | °C |  |  | Y | DHC冷水返送ヘッダ
DHC-CHW-L.FLW | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Intake flow | AI | 4-20mA | L/min |  |  | Y
DHC-CHW-L.CV | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Intake control valve | AO | 0-10V | % | Y |  |  | Modulate to load; DHC primary
DHC-CHW-L.CVFB | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Intake valve position fb | AI | 4-20mA | %
DHC-CHW-L.ISOL | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Intake isolation valve open/close | BO | DO relay | - | Y
DHC-CHW-L.ISOL-ST | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Isolation valve status | BI | DI dry contact | - |  | Y
DHC-CHW-L.SEQ | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Source sequence changeover (DHC<->chiller) | BO | DO relay | - | Y |  |  | 順序切替; DHC lead, chiller backup
DHC-CHW-L.ENERGY | DHC interface | DHC-CHW-L | DHC chilled-water intake | B2F chilled-water intake (low-rise) | LCP-B2 | DDC-B2-02 | Chilled-water energy meter | AI | Pulse/Modbus | GJ |  |  | Y | Thermal-demand control
DHC-CHW-H.ST | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Intake (supply header) temp | AI | 4-20mA | °C |  | Y | Y | DHC冷水受入ヘッダ ~7°C
DHC-CHW-H.RT | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Return header temp | AI | 4-20mA | °C |  |  | Y | DHC冷水返送ヘッダ
DHC-CHW-H.FLW | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Intake flow | AI | 4-20mA | L/min |  |  | Y
DHC-CHW-H.CV | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Intake control valve | AO | 0-10V | % | Y |  |  | Modulate to load; DHC primary
DHC-CHW-H.CVFB | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Intake valve position fb | AI | 4-20mA | %
DHC-CHW-H.ISOL | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Intake isolation valve open/close | BO | DO relay | - | Y
DHC-CHW-H.ISOL-ST | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Isolation valve status | BI | DI dry contact | - |  | Y
DHC-CHW-H.SEQ | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Source sequence changeover (DHC<->chiller) | BO | DO relay | - | Y |  |  | 順序切替; DHC lead, chiller backup
DHC-CHW-H.ENERGY | DHC interface | DHC-CHW-H | DHC chilled-water intake | PH chilled-water intake (high-rise) | LCP-PH | DDC-PH-08 | Chilled-water energy meter | AI | Pulse/Modbus | GJ |  |  | Y | Thermal-demand control
DHC-STEAM-L.HPRESS | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Steam header pressure | AI | 4-20mA | MPa |  | Y | Y
DHC-STEAM-L.HTEMP | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Steam header temp | AI | 4-20mA | °C |  |  | Y
DHC-STEAM-L.PRV | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Pressure-reducing / control valve | AO | 0-10V | % | Y
DHC-STEAM-L.ISOL | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Main isolation valve open/close | BO | DO relay | - | Y |  |  | Season enable + OA lockout
DHC-STEAM-L.ISOL-ST | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Isolation valve status | BI | DI dry contact | - |  | Y
DHC-STEAM-L.COND-T | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Condensate temp | AI | 4-20mA | °C
DHC-STEAM-L.ENERGY | DHC interface | DHC-STEAM-L | DHC steam interface | B2F low-rise steam main | LCP-B2 | DDC-B2-03 | Steam energy meter | AI | Pulse/Modbus | GJ |  |  | Y | For thermal-demand control
DHC-STEAM-H.HPRESS | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Steam header pressure | AI | 4-20mA | MPa |  | Y | Y
DHC-STEAM-H.HTEMP | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Steam header temp | AI | 4-20mA | °C |  |  | Y
DHC-STEAM-H.PRV | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Pressure-reducing / control valve | AO | 0-10V | % | Y
DHC-STEAM-H.ISOL | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Main isolation valve open/close | BO | DO relay | - | Y |  |  | Season enable + OA lockout
DHC-STEAM-H.ISOL-ST | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Isolation valve status | BI | DI dry contact | - |  | Y
DHC-STEAM-H.COND-T | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Condensate temp | AI | 4-20mA | °C
DHC-STEAM-H.ENERGY | DHC interface | DHC-STEAM-H | DHC steam interface | Rooftop/PH high-rise steam main | LCP-PH | DDC-PH-09 | Steam energy meter | AI | Pulse/Modbus | GJ |  |  | Y | For thermal-demand control
AC-1.RUN | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-1.TRIP | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-1.SS | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-1.SPD | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-1.SAT | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-1.RAT | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-1.CCV | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-1.HCV | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-1.FLT | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-1.OAD | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Outdoor-air damper | AO | 0-10V | % | Y
AC-1.FRZ | Air side | AC-1 | AHU (public/kitchen) | B3-4F service elevator hall | LCP-B2 | DDC-B2-04 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-2.RUN | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-2.TRIP | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-2.SS | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-2.SPD | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-2.SAT | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-2.RAT | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-2.CCV | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-2.FLT | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-2.OAD | Air side | AC-2 | AHU (public/kitchen) | Mid banquet / B1F back corridor / F&B office | LCP-B2 | DDC-B2-04 | Outdoor-air damper | AO | 0-10V | % | Y
AC-3.RUN | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-3.TRIP | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-3.SS | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-3.SPD | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-3.SAT | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-3.RAT | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-3.CCV | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-3.FLT | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-3.OAD | Air side | AC-3 | AHU (public/kitchen) | B1F guest lift lobby & anteroom | LCP-B2 | DDC-B2-04 | Outdoor-air damper | AO | 0-10V | % | Y
AC-4.RUN | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-4.TRIP | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-4.SS | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-4.SPD | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-4.SPDFB | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-4.SAT | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-4.RAT | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-4.CCV | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-4.FLT | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-4.OAD | Air side | AC-4 | AHU (public/kitchen) | B1F banquet lobby | LCP-B2 | DDC-B2-05 | Outdoor-air damper | AO | 0-10V | % | Y
AC-5.RUN | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-5.TRIP | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-5.SS | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-5.SPD | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-5.SPDFB | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-5.SAT | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-5.RAT | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-5.CCV | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-5.HCV | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-5.FLT | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-5.OAD | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Outdoor-air damper | AO | 0-10V | % | Y
AC-5.FRZ | Air side | AC-5 | AHU (public/kitchen) | Guardmanger & Bakery kitchen | LCP-B2 | DDC-B2-05 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-6.RUN | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-6.TRIP | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-6.SS | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-6.SPD | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-6.SPDFB | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-6.SAT | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-6.RAT | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-6.CCV | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-6.HCV | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-6.FLT | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-6.OAD | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Outdoor-air damper | AO | 0-10V | % | Y
AC-6.FRZ | Air side | AC-6 | AHU (public/kitchen) | C kitchen | LCP-B2 | DDC-B2-05 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-7.RUN | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-7.TRIP | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-7.SS | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-7.SPD | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-7.SPDFB | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-7.SAT | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-7.RAT | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-7.CCV | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-7.HCV | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-7.FLT | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-7.OAD | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-7.FRZ | Air side | AC-7 | AHU (public/kitchen) | Main kitchen | LCP-1F | DDC-1F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-8.RUN | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-8.TRIP | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-8.SS | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-8.SPD | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-8.SAT | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-8.RAT | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-8.CCV | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-8.HCV | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-8.FLT | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-8.OAD | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-8.FRZ | Air side | AC-8 | AHU (public/kitchen) | Cascade Cafe hall | LCP-2F | DDC-2F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-9.RUN | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-9.TRIP | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-9.SS | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-9.SPD | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | INFERRED / no INV control per schedule
AC-9.SAT | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-9.RAT | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-9.CCV | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-9.HCV | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-9.FLT | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-9.OAD | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-9.FRZ | Air side | AC-9 | AHU (public/kitchen) | Cascade kitchen | LCP-2F | DDC-2F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-10.RUN | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-10.TRIP | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-10.SS | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-10.SPD | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-10.SPDFB | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-10.SAT | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-10.RAT | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-10.CCV | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-10.HCV | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-10.HUM | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Steam humidifier valve | AO | 0-10V | % | Y
AC-10.RH | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-10.FLT | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-10.OAD | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-10.FRZ | Air side | AC-10 | AHU (public/kitchen) | Atrium lobby/lounge | LCP-2F | DDC-2F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-11.RUN | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-11.TRIP | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-11.SS | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-11.SPD | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-11.SPDFB | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-11.SAT | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-11.RAT | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-11.CCV | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-11.HCV | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-11.FLT | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-11.OAD | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Outdoor-air damper | AO | 0-10V | % | Y
AC-11.FRZ | Air side | AC-11 | AHU (public/kitchen) | Prominence I | LCP-2F | DDC-2F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-12.RUN | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-12.TRIP | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-12.SS | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-12.SPD | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-12.SPDFB | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-12.SAT | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-12.RAT | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-12.CCV | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-12.HCV | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-12.FLT | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-12.OAD | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Outdoor-air damper | AO | 0-10V | % | Y
AC-12.FRZ | Air side | AC-12 | AHU (public/kitchen) | Prominence II | LCP-2F | DDC-2F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-13.RUN | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-13.TRIP | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-13.SS | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-13.SPD | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-13.SPDFB | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-13.SAT | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-13.RAT | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-13.CCV | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-13.HCV | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-13.FLT | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-13.OAD | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Outdoor-air damper | AO | 0-10V | % | Y
AC-13.FRZ | Air side | AC-13 | AHU (public/kitchen) | Prominence III | LCP-2F | DDC-2F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-14.RUN | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-14.TRIP | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-14.SS | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-14.SPD | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-14.SPDFB | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-14.SAT | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-14.RAT | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-14.CCV | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-14.HCV | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-14.HUM | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Steam humidifier valve | AO | 0-10V | % | Y
AC-14.RH | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-14.FLT | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-14.OAD | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-14.FRZ | Air side | AC-14 | AHU (public/kitchen) | Unkai hall | LCP-3F | DDC-3F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-15.RUN | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-15.TRIP | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-15.SS | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-15.SPD | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-15.SPDFB | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-15.SAT | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-15.RAT | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-15.CCV | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-15.HCV | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-15.FLT | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-15.OAD | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-15.FRZ | Air side | AC-15 | AHU (public/kitchen) | Karin/Kenzan kitchen | LCP-3F | DDC-3F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-16.RUN | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-16.TRIP | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-16.SS | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-16.SPD | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-16.SPDFB | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-16.SAT | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-16.RAT | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-16.CCV | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-16.HCV | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-16.FLT | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-16.OAD | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-16.FRZ | Air side | AC-16 | AHU (public/kitchen) | DaVinci kitchen | LCP-3F | DDC-3F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-17.RUN | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-17.TRIP | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-17.SS | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-17.SPD | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-17.SPDFB | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-17.SAT | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-17.RAT | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-17.CCV | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-17.HCV | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-17.FLT | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-17.OAD | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-17.FRZ | Air side | AC-17 | AHU (public/kitchen) | Unkai kitchen | LCP-4F | DDC-4F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-18.RUN | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-18.TRIP | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-18.SS | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-18.SPD | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-18.SPDFB | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-18.SAT | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-18.RAT | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-18.CCV | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-18.HCV | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-18.FLT | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-18.OAD | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-18.FRZ | Air side | AC-18 | AHU (public/kitchen) | Steakhouse kitchen | LCP-4F | DDC-4F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-19.RUN | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-19.TRIP | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-19.SS | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-19.SPD | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-19.SPDFB | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-19.SAT | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-19.RAT | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-19.CCV | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-19.HCV | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-19.HUM | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Steam humidifier valve | AO | 0-10V | % | Y
AC-19.RH | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-19.FLT | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-19.OAD | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Outdoor-air damper | AO | 0-10V | % | Y
AC-19.FRZ | Air side | AC-19 | AHU (public/kitchen) | Steakhouse hall | LCP-4F | DDC-4F-01 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-20.RUN | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-20.TRIP | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-20.SS | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-20.SPD | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-20.SPDFB | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-20.SAT | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-20.RAT | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-20.CCV | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-20.HCV | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-20.FLT | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-20.OAD | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Outdoor-air damper | AO | 0-10V | % | Y
AC-20.FRZ | Air side | AC-20 | AHU (public/kitchen) | Poolside snack/pantry (4F) | LCP-4F | DDC-4F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-21.RUN | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-21.TRIP | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-21.SS | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-21.SPD | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-21.SPDFB | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-21.SAT | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-21.RAT | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-21.CCV | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-21.HCV | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-21.FLT | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-21.OAD | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Outdoor-air damper | AO | 0-10V | % | Y
AC-21.FRZ | Air side | AC-21 | AHU (public/kitchen) | 5F staff canteen kitchen | LCP-4F | DDC-4F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-22.RUN | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-22.TRIP | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-22.SS | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-22.SPD | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-22.SPDFB | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-22.SAT | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-22.RAT | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-22.CCV | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-22.HCV | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-22.FLT | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-22.OAD | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Outdoor-air damper | AO | 0-10V | % | Y
AC-22.FRZ | Air side | AC-22 | AHU (public/kitchen) | PG/Mixx kitchen (36F) | LCP-PH | DDC-PH-10 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-23.RUN | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-23.TRIP | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-23.SS | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-23.SPD | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-23.SPDFB | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-23.SAT | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | Kitchen SAT 5-12°C
AC-23.RAT | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-23.CCV | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-23.HCV | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-23.FLT | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-23.OAD | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Outdoor-air damper | AO | 0-10V | % | Y
AC-23.FRZ | Air side | AC-23 | AHU (public/kitchen) | Akasaka kitchen (37F) | LCP-PH | DDC-PH-10 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-24.RUN | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-24.TRIP | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-24.SS | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-24.SPD | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-24.SPDFB | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-24.SAT | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-24.RAT | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-24.CCV | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-24.HCV | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-24.HUM | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Steam humidifier valve | AO | 0-10V | % | Y
AC-24.RH | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-24.FLT | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-24.OAD | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Outdoor-air damper | AO | 0-10V | % | Y
AC-24.FRZ | Air side | AC-24 | AHU (public/kitchen) | Akasaka hall / Libra / Aries | LCP-PH | DDC-PH-10 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-25.RUN | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-25.TRIP | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-25.SS | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-25.SPD | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-25.SPDFB | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-25.SAT | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-25.RAT | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-25.CCV | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-25.HCV | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-25.FLT | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-25.OAD | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Outdoor-air damper | AO | 0-10V | % | Y
AC-25.FRZ | Air side | AC-25 | AHU (public/kitchen) | Sirius hall & kitchen | LCP-PH | DDC-PH-11 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-26.RUN | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-26.TRIP | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-26.SS | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-26.SPD | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-26.SPDFB | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-26.SAT | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-26.RAT | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-26.CCV | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-26.HCV | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-26.FLT | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-26.OAD | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Outdoor-air damper | AO | 0-10V | % | Y
AC-26.FRZ | Air side | AC-26 | AHU (public/kitchen) | Banquet-service office (B2F) | LCP-B2 | DDC-B2-06 | Freeze protection stat | BI | DI dry contact | - |  | Y
AC-27.RUN | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Supply fan run status | BI | DI dry contact | - |  |  | Y
AC-27.TRIP | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Supply fan fault | BI | DI dry contact | - |  | Y
AC-27.SS | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time/event schedule; banquet 'occ by event'
AC-27.SPD | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV output schedule 0.4-1.0
AC-27.SPDFB | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
AC-27.SAT | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Supply air temp | AI | 4-20mA | °C | Y | Y | Y | SAT/RAT setpoint schedule
AC-27.RAT | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Return air temp | AI | 4-20mA | °C |  |  | Y
AC-27.CCV | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Cooling coil (CHW) valve | AO | 0-10V | % | Y |  |  | PID to SAT; zero-energy band
AC-27.HCV | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband vs CCV
AC-27.HUM | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Steam humidifier valve | AO | 0-10V | % | Y
AC-27.RH | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Return/space humidity | AI | 4-20mA | %RH |  |  | Y
AC-27.FLT | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
AC-27.OAD | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Outdoor-air damper | AO | 0-10V | % | Y
AC-27.FRZ | Air side | AC-27 | AHU (public/kitchen) | Club Lounge (35F) - 4-pipe | LCP-PH | DDC-PH-11 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-1.RUN | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-1.TRIP | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-1.SS | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-1.SPD | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-1.SAT | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-1.OAT | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-1.OARH | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-1.CCV | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-1.HCV | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-1.HUM | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-1.FLT | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-1.FRZ | Air side | EVU-1 | Outdoor-air unit (OAU) | 1F ceremony/photo/dress/beauty/corridor | LCP-1F | DDC-1F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-2.RUN | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-2.TRIP | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-2.SS | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-2.SPD | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-2.SAT | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-2.OAT | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-2.OARH | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-2.CCV | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-2.HCV | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-2.HUM | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-2.FLT | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-2.FRZ | Air side | EVU-2 | Outdoor-air unit (OAU) | 1F small banquet/corridor/store | LCP-1F | DDC-1F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-3.RUN | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-3.TRIP | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-3.SS | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-3.SPD | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-3.SAT | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-3.OAT | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-3.OARH | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-3.CCV | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-3.HCV | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-3.HUM | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-3.FLT | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-3.FRZ | Air side | EVU-3 | Outdoor-air unit (OAU) | Banquet entrance lobby & bell room | LCP-1F | DDC-1F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-4.RUN | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-4.TRIP | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-4.SS | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-4.SPD | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-4.SAT | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-4.OAT | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-4.OARH | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-4.CCV | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-4.HCV | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-4.HUM | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-4.FLT | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-4.FRZ | Air side | EVU-4 | Outdoor-air unit (OAU) | 2F office & CPU room | LCP-2F | DDC-2F-03 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-5.RUN | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-5.TRIP | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-5.SS | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-5.SPD | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-5.SAT | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-5.OAT | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-5.OARH | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-5.CCV | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-5.HCV | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-5.HUM | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-5.FLT | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-5.FRZ | Air side | EVU-5 | Outdoor-air unit (OAU) | 2F tenants/shops | LCP-2F | DDC-2F-03 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-6.RUN | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-6.TRIP | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-6.SS | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-6.SPD | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-6.SAT | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-6.OAT | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-6.OARH | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-6.CCV | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-6.HCV | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-6.HUM | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-6.FLT | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-6.FRZ | Air side | EVU-6 | Outdoor-air unit (OAU) | Prominence (B1F precool) | LCP-2F | DDC-2F-03 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-7.RUN | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-7.TRIP | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-7.SS | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-7.SPD | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-7.SAT | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-7.OAT | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-7.OARH | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-7.CCV | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-7.HCV | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-7.HUM | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-7.FLT | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-7.FRZ | Air side | EVU-7 | Outdoor-air unit (OAU) | 3F Karin/Kenzan/DaVinci/chapel | LCP-3F | DDC-3F-02 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-8.RUN | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-8.TRIP | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-8.SS | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-8.SPD | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-8.SPDFB | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-8.SAT | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-8.OAT | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-8.OARH | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-8.CCV | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-8.HCV | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-8.HUM | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-8.FLT | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-8.FRZ | Air side | EVU-8 | Outdoor-air unit (OAU) | Low-rise guest rooms N (6-20F) | LCP-4F | DDC-4F-03 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-9.RUN | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-9.TRIP | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-9.SS | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-9.SPD | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-9.SPDFB | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-9.SAT | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-9.OAT | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-9.OARH | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-9.CCV | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-9.HCV | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-9.HUM | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-9.FLT | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-9.FRZ | Air side | EVU-9 | Outdoor-air unit (OAU) | Low-rise guest rooms SE (6-20F) | LCP-4F | DDC-4F-03 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-10.RUN | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-10.TRIP | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-10.SS | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-10.SPD | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-10.SPDFB | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-10.SAT | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-10.OAT | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-10.OARH | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-10.CCV | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-10.HCV | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-10.HUM | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-10.FLT | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-10.FRZ | Air side | EVU-10 | Outdoor-air unit (OAU) | Low-rise guest rooms SW (6-20F) | LCP-4F | DDC-4F-03 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-11.RUN | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-11.TRIP | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-11.SS | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-11.SPD | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-11.SPDFB | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-11.SAT | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-11.OAT | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-11.OARH | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-11.CCV | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-11.HCV | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-11.HUM | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-11.FLT | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-11.FRZ | Air side | EVU-11 | Outdoor-air unit (OAU) | High-rise guest rooms N (21-35F) | LCP-PH | DDC-PH-12 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-12.RUN | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-12.TRIP | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-12.SS | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-12.SPD | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-12.SPDFB | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-12.SAT | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-12.OAT | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-12.OARH | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-12.CCV | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-12.HCV | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-12.HUM | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-12.FLT | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-12.FRZ | Air side | EVU-12 | Outdoor-air unit (OAU) | High-rise guest rooms SE (21-35F) | LCP-PH | DDC-PH-12 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-13.RUN | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-13.TRIP | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-13.SS | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-13.SPD | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Supply fan VFD (INV) speed | AO | 0-10V | % | Y |  |  | INV schedule; demand vent
EVU-13.SPDFB | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Supply fan speed feedback | AI | 4-20mA | % |  |  | Y
EVU-13.SAT | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-13.OAT | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-13.OARH | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-13.CCV | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-13.HCV | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-13.HUM | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-13.FLT | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-13.FRZ | Air side | EVU-13 | Outdoor-air unit (OAU) | High-rise guest rooms SW (21-35F) | LCP-PH | DDC-PH-12 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-14.RUN | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-14.TRIP | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-14.SS | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-14.SPD | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-14.SAT | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-14.OAT | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-14.OARH | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-14.CCV | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-14.HCV | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-14.HUM | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-14.FLT | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-14.FRZ | Air side | EVU-14 | Outdoor-air unit (OAU) | 36F office/Mixx | LCP-PH | DDC-PH-13 | Freeze protection stat | BI | DI dry contact | - |  | Y
EVU-15.RUN | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Supply fan run status | BI | DI dry contact | - |  |  | Y
EVU-15.TRIP | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Supply fan fault | BI | DI dry contact | - |  | Y
EVU-15.SS | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Supply fan start/stop | BO | DO relay | - | Y |  |  | Time schedule; night setback
EVU-15.SPD | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Supply fan speed (fixed) | AO | 0-10V | % |  |  |  | No INV control per schedule
EVU-15.SAT | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Supply (off-coil) air temp | AI | 4-20mA | °C | Y | Y | Y | Seasonal SAT reset
EVU-15.OAT | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Outdoor-air temp (unit inlet) | AI | 4-20mA | °C |  |  | Y
EVU-15.OARH | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y
EVU-15.CCV | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Cooling coil (CHW) valve | AO | 0-10V | % | Y
EVU-15.HCV | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Heating coil (steam) valve | AO | 0-10V | % | Y |  |  | Season enable; deadband
EVU-15.HUM | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Steam humidifier valve | AO | 0-10V | % | Y
EVU-15.FLT | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Filter dirty (DP) | BI | DI dry contact | - |  | Y
EVU-15.FRZ | Air side | EVU-15 | Outdoor-air unit (OAU) | 36F PG hall/rooms/pantry, Mixx bar/hall | LCP-PH | DDC-PH-13 | Freeze protection stat | BI | DI dry contact | - |  | Y
FCU-L-N.EN | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-N.MODE | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-N.CWV | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-N.HWV | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-N.CWBV-F | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-N.HWBV-F | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-N.RT | Air side | FCU-L-N | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (N) | LCP-4F | DDC-4F-04 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-S.EN | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-S.MODE | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-S.CWV | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-S.HWV | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-S.CWBV-F | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-S.HWBV-F | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-S.RT | Air side | FCU-L-S | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (S) | LCP-4F | DDC-4F-04 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-SE.EN | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-SE.MODE | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-SE.CWV | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-SE.HWV | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-SE.CWBV-F | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-SE.HWBV-F | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-SE.RT | Air side | FCU-L-SE | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SE) | LCP-4F | DDC-4F-04 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-L-SW.EN | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-L-SW.MODE | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-L-SW.CWV | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-L-SW.HWV | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-L-SW.CWBV-F | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-L-SW.HWBV-F | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-L-SW.RT | Air side | FCU-L-SW | FCU zone group (4-pipe) | Low-rise guest rooms 5-20F (SW) | LCP-4F | DDC-4F-05 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-N.EN | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-N.MODE | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-N.CWV | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-N.HWV | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-N.CWBV-F | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-N.HWBV-F | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-N.RT | Air side | FCU-H-N | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (N) | LCP-PH | DDC-PH-14 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-S.EN | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-S.MODE | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-S.CWV | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-S.HWV | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-S.CWBV-F | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-S.HWBV-F | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-S.RT | Air side | FCU-H-S | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (S) | LCP-PH | DDC-PH-14 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-SE.EN | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-SE.MODE | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-SE.CWV | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-SE.HWV | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-SE.CWBV-F | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-SE.HWBV-F | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-SE.RT | Air side | FCU-H-SE | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SE) | LCP-PH | DDC-PH-14 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-H-SW.EN | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Group enable / schedule | BO | DO relay | - | Y |  |  | DHC 4-pipe; season changeover
FCU-H-SW.MODE | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-H-SW.CWV | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-H-SW.HWV | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-H-SW.CWBV-F | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-H-SW.HWBV-F | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-H-SW.RT | Air side | FCU-H-SW | FCU zone group (4-pipe) | High-rise guest rooms 20-35F (SW) | LCP-PH | DDC-PH-15 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
FCU-3637.EN | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Group enable / schedule | BO | DO relay | - | Y |  |  | 36/37F: free-cooling changeover
FCU-3637.MODE | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Cooling/Heating changeover status | BI | DI dry contact | - |  |  |  | 順序/季節切替
FCU-3637.CWV | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Chilled-water group valve | AO | 0-10V | % | Y
FCU-3637.HWV | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Hot-water group valve | AO | 0-10V | % | Y |  |  | Deadband vs cooling
FCU-3637.CWBV-F | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Chilled-water BV batch fault | BI | DI dry contact | - |  | Y |  | 冷水BV一括故障
FCU-3637.HWBV-F | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Hot-water BV batch fault | BI | DI dry contact | - |  | Y |  | 温水BV一括故障
FCU-3637.RT | Air side | FCU-3637 | FCU zone group (4-pipe) | 36/37F FCU (4-pipe + free cooling) | LCP-PH | DDC-PH-15 | Zone reference/return temp | AI | 4-20mA | °C | Y |  | Y
SF-6.SS | Ventilation | SF-6 | Exhaust/supply fan | Serves AC-1 (B3-4F service elevator hall) | LCP-B2 | DDC-B2-07 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
SF-6.RUN | Ventilation | SF-6 | Exhaust/supply fan | Serves AC-1 (B3-4F service elevator hall) | LCP-B2 | DDC-B2-07 | Run status | BI | DI dry contact | - |  |  | Y
SF-6.TRIP | Ventilation | SF-6 | Exhaust/supply fan | Serves AC-1 (B3-4F service elevator hall) | LCP-B2 | DDC-B2-07 | Fault | BI | DI dry contact | - |  | Y
EF-2-1.SS | Ventilation | EF-2-1 | Exhaust/supply fan | Serves AC-8 (Cascade Cafe hall) | LCP-2F | DDC-2F-04 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-2-1.RUN | Ventilation | EF-2-1 | Exhaust/supply fan | Serves AC-8 (Cascade Cafe hall) | LCP-2F | DDC-2F-04 | Run status | BI | DI dry contact | - |  |  | Y
EF-2-1.TRIP | Ventilation | EF-2-1 | Exhaust/supply fan | Serves AC-8 (Cascade Cafe hall) | LCP-2F | DDC-2F-04 | Fault | BI | DI dry contact | - |  | Y
EF-28.SS | Ventilation | EF-28 | Exhaust/supply fan | Serves AC-5 (Guardmanger & Bakery kitchen) | LCP-B2 | DDC-B2-07 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-28.RUN | Ventilation | EF-28 | Exhaust/supply fan | Serves AC-5 (Guardmanger & Bakery kitchen) | LCP-B2 | DDC-B2-07 | Run status | BI | DI dry contact | - |  |  | Y
EF-28.TRIP | Ventilation | EF-28 | Exhaust/supply fan | Serves AC-5 (Guardmanger & Bakery kitchen) | LCP-B2 | DDC-B2-07 | Fault | BI | DI dry contact | - |  | Y
EF-32.SS | Ventilation | EF-32 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-B2 | DDC-B2-07 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-32.RUN | Ventilation | EF-32 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-B2 | DDC-B2-07 | Run status | BI | DI dry contact | - |  |  | Y
EF-32.TRIP | Ventilation | EF-32 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-B2 | DDC-B2-07 | Fault | BI | DI dry contact | - |  | Y
EF-33.SS | Ventilation | EF-33 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-B2 | DDC-B2-08 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-33.RUN | Ventilation | EF-33 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-B2 | DDC-B2-08 | Run status | BI | DI dry contact | - |  |  | Y
EF-33.TRIP | Ventilation | EF-33 | Exhaust/supply fan | Serves AC-6 (C kitchen) | LCP-B2 | DDC-B2-08 | Fault | BI | DI dry contact | - |  | Y
EF-41.SS | Ventilation | EF-41 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-41.RUN | Ventilation | EF-41 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 | Run status | BI | DI dry contact | - |  |  | Y
EF-41.TRIP | Ventilation | EF-41 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 | Fault | BI | DI dry contact | - |  | Y
EF-42.SS | Ventilation | EF-42 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-42.RUN | Ventilation | EF-42 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 | Run status | BI | DI dry contact | - |  |  | Y
EF-42.TRIP | Ventilation | EF-42 | Exhaust/supply fan | Serves AC-7 (Main kitchen) | LCP-1F | DDC-1F-03 | Fault | BI | DI dry contact | - |  | Y
EF-46.SS | Ventilation | EF-46 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-46.RUN | Ventilation | EF-46 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 | Run status | BI | DI dry contact | - |  |  | Y
EF-46.TRIP | Ventilation | EF-46 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 | Fault | BI | DI dry contact | - |  | Y
EF-47.SS | Ventilation | EF-47 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-47.RUN | Ventilation | EF-47 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 | Run status | BI | DI dry contact | - |  |  | Y
EF-47.TRIP | Ventilation | EF-47 | Exhaust/supply fan | Serves AC-9 (Cascade kitchen) | LCP-2F | DDC-2F-04 | Fault | BI | DI dry contact | - |  | Y
EF-54.SS | Ventilation | EF-54 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-06 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-54.RUN | Ventilation | EF-54 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-06 | Run status | BI | DI dry contact | - |  |  | Y
EF-54.TRIP | Ventilation | EF-54 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-06 | Fault | BI | DI dry contact | - |  | Y
EF-55.SS | Ventilation | EF-55 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-06 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-55.RUN | Ventilation | EF-55 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-06 | Run status | BI | DI dry contact | - |  |  | Y
EF-55.TRIP | Ventilation | EF-55 | Exhaust/supply fan | Serves AC-17 (Unkai kitchen) | LCP-4F | DDC-4F-06 | Fault | BI | DI dry contact | - |  | Y
EF-56.SS | Ventilation | EF-56 | Exhaust/supply fan | Serves AC-14 (Unkai hall) | LCP-3F | DDC-3F-03 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-56.RUN | Ventilation | EF-56 | Exhaust/supply fan | Serves AC-14 (Unkai hall) | LCP-3F | DDC-3F-03 | Run status | BI | DI dry contact | - |  |  | Y
EF-56.TRIP | Ventilation | EF-56 | Exhaust/supply fan | Serves AC-14 (Unkai hall) | LCP-3F | DDC-3F-03 | Fault | BI | DI dry contact | - |  | Y
EF-57.SS | Ventilation | EF-57 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-06 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-57.RUN | Ventilation | EF-57 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-06 | Run status | BI | DI dry contact | - |  |  | Y
EF-57.TRIP | Ventilation | EF-57 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-06 | Fault | BI | DI dry contact | - |  | Y
EF-58.SS | Ventilation | EF-58 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-07 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-58.RUN | Ventilation | EF-58 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-07 | Run status | BI | DI dry contact | - |  |  | Y
EF-58.TRIP | Ventilation | EF-58 | Exhaust/supply fan | Serves AC-18 (Steakhouse kitchen) | LCP-4F | DDC-4F-07 | Fault | BI | DI dry contact | - |  | Y
EF-59.SS | Ventilation | EF-59 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-07 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-59.RUN | Ventilation | EF-59 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-07 | Run status | BI | DI dry contact | - |  |  | Y
EF-59.TRIP | Ventilation | EF-59 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-07 | Fault | BI | DI dry contact | - |  | Y
EF-59-2.SS | Ventilation | EF-59-2 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-07 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-59-2.RUN | Ventilation | EF-59-2 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-07 | Run status | BI | DI dry contact | - |  |  | Y
EF-59-2.TRIP | Ventilation | EF-59-2 | Exhaust/supply fan | Serves AC-19 (Steakhouse hall) | LCP-4F | DDC-4F-07 | Fault | BI | DI dry contact | - |  | Y
EF-60.SS | Ventilation | EF-60 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-03 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-60.RUN | Ventilation | EF-60 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-03 | Run status | BI | DI dry contact | - |  |  | Y
EF-60.TRIP | Ventilation | EF-60 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-03 | Fault | BI | DI dry contact | - |  | Y
EF-61.SS | Ventilation | EF-61 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-03 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-61.RUN | Ventilation | EF-61 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-03 | Run status | BI | DI dry contact | - |  |  | Y
EF-61.TRIP | Ventilation | EF-61 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-03 | Fault | BI | DI dry contact | - |  | Y
EF-62.SS | Ventilation | EF-62 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-04 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-62.RUN | Ventilation | EF-62 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-04 | Run status | BI | DI dry contact | - |  |  | Y
EF-62.TRIP | Ventilation | EF-62 | Exhaust/supply fan | Serves AC-16 (DaVinci kitchen) | LCP-3F | DDC-3F-04 | Fault | BI | DI dry contact | - |  | Y
EF-67.SS | Ventilation | EF-67 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-08 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-67.RUN | Ventilation | EF-67 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-08 | Run status | BI | DI dry contact | - |  |  | Y
EF-67.TRIP | Ventilation | EF-67 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-08 | Fault | BI | DI dry contact | - |  | Y
EF-69.SS | Ventilation | EF-69 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-69.RUN | Ventilation | EF-69 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | Run status | BI | DI dry contact | - |  |  | Y
EF-69.TRIP | Ventilation | EF-69 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | Fault | BI | DI dry contact | - |  | Y
EF-70.SS | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-70.RUN | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | Run status | BI | DI dry contact | - |  |  | Y
EF-70.TRIP | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | Fault | BI | DI dry contact | - |  | Y
EF-70.SPD | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | VFD (INV) speed command | AO | 0-10V | % | Y
EF-70.SPDFB | Ventilation | EF-70 | Exhaust/supply fan | Serves AC-21 (5F staff canteen kitchen) | LCP-4F | DDC-4F-08 | VFD speed feedback | AI | 4-20mA | %
EF-71.SS | Ventilation | EF-71 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-09 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-71.RUN | Ventilation | EF-71 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-09 | Run status | BI | DI dry contact | - |  |  | Y
EF-71.TRIP | Ventilation | EF-71 | Exhaust/supply fan | Serves AC-20 (Poolside snack/pantry (4F)) | LCP-4F | DDC-4F-09 | Fault | BI | DI dry contact | - |  | Y
EF-76.SS | Ventilation | EF-76 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-76.RUN | Ventilation | EF-76 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 | Run status | BI | DI dry contact | - |  |  | Y
EF-76.TRIP | Ventilation | EF-76 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 | Fault | BI | DI dry contact | - |  | Y
EF-77.SS | Ventilation | EF-77 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-77.RUN | Ventilation | EF-77 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 | Run status | BI | DI dry contact | - |  |  | Y
EF-77.TRIP | Ventilation | EF-77 | Exhaust/supply fan | Serves AC-15 (Karin/Kenzan kitchen) | LCP-3F | DDC-3F-04 | Fault | BI | DI dry contact | - |  | Y
EF-82.SS | Ventilation | EF-82 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-82.RUN | Ventilation | EF-82 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | Run status | BI | DI dry contact | - |  |  | Y
EF-82.TRIP | Ventilation | EF-82 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | Fault | BI | DI dry contact | - |  | Y
EF-83.SS | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-83.RUN | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | Run status | BI | DI dry contact | - |  |  | Y
EF-83.TRIP | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | Fault | BI | DI dry contact | - |  | Y
EF-83.SPD | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | VFD (INV) speed command | AO | 0-10V | % | Y
EF-83.SPDFB | Ventilation | EF-83 | Exhaust/supply fan | Serves AC-22 (PG/Mixx kitchen (36F)) | LCP-PH | DDC-PH-16 | VFD speed feedback | AI | 4-20mA | %
EF-84.SS | Ventilation | EF-84 | Exhaust/supply fan | Serves AC-23 (Akasaka kitchen (37F)) | LCP-PH | DDC-PH-16 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-84.RUN | Ventilation | EF-84 | Exhaust/supply fan | Serves AC-23 (Akasaka kitchen (37F)) | LCP-PH | DDC-PH-16 | Run status | BI | DI dry contact | - |  |  | Y
EF-84.TRIP | Ventilation | EF-84 | Exhaust/supply fan | Serves AC-23 (Akasaka kitchen (37F)) | LCP-PH | DDC-PH-16 | Fault | BI | DI dry contact | - |  | Y
EF-85.SS | Ventilation | EF-85 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-PH | DDC-PH-17 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-85.RUN | Ventilation | EF-85 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-PH | DDC-PH-17 | Run status | BI | DI dry contact | - |  |  | Y
EF-85.TRIP | Ventilation | EF-85 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-PH | DDC-PH-17 | Fault | BI | DI dry contact | - |  | Y
EF-86.SS | Ventilation | EF-86 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-PH | DDC-PH-17 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-86.RUN | Ventilation | EF-86 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-PH | DDC-PH-17 | Run status | BI | DI dry contact | - |  |  | Y
EF-86.TRIP | Ventilation | EF-86 | Exhaust/supply fan | Serves AC-24 (Akasaka hall / Libra / Aries) | LCP-PH | DDC-PH-17 | Fault | BI | DI dry contact | - |  | Y
EF-89.SS | Ventilation | EF-89 | Exhaust/supply fan | Serves AC-25 (Sirius hall & kitchen) | LCP-PH | DDC-PH-17 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-89.RUN | Ventilation | EF-89 | Exhaust/supply fan | Serves AC-25 (Sirius hall & kitchen) | LCP-PH | DDC-PH-17 | Run status | BI | DI dry contact | - |  |  | Y
EF-89.TRIP | Ventilation | EF-89 | Exhaust/supply fan | Serves AC-25 (Sirius hall & kitchen) | LCP-PH | DDC-PH-17 | Fault | BI | DI dry contact | - |  | Y
EF-97.SS | Ventilation | EF-97 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-B2 | DDC-B2-08 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-97.RUN | Ventilation | EF-97 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-B2 | DDC-B2-08 | Run status | BI | DI dry contact | - |  |  | Y
EF-97.TRIP | Ventilation | EF-97 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-B2 | DDC-B2-08 | Fault | BI | DI dry contact | - |  | Y
EF-98.SS | Ventilation | EF-98 | Exhaust/supply fan | Serves AC-27 (Club Lounge (35F) - 4-pipe) | LCP-PH | DDC-PH-18 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
EF-98.RUN | Ventilation | EF-98 | Exhaust/supply fan | Serves AC-27 (Club Lounge (35F) - 4-pipe) | LCP-PH | DDC-PH-18 | Run status | BI | DI dry contact | - |  |  | Y
EF-98.TRIP | Ventilation | EF-98 | Exhaust/supply fan | Serves AC-27 (Club Lounge (35F) - 4-pipe) | LCP-PH | DDC-PH-18 | Fault | BI | DI dry contact | - |  | Y
RF-7.SS | Ventilation | RF-7 | Exhaust/supply fan | Serves AC-3 (B1F guest lift lobby & anteroom) | LCP-B2 | DDC-B2-08 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
RF-7.RUN | Ventilation | RF-7 | Exhaust/supply fan | Serves AC-3 (B1F guest lift lobby & anteroom) | LCP-B2 | DDC-B2-08 | Run status | BI | DI dry contact | - |  |  | Y
RF-7.TRIP | Ventilation | RF-7 | Exhaust/supply fan | Serves AC-3 (B1F guest lift lobby & anteroom) | LCP-B2 | DDC-B2-08 | Fault | BI | DI dry contact | - |  | Y
RF-8.SS | Ventilation | RF-8 | Exhaust/supply fan | Serves AC-4 (B1F banquet lobby) | LCP-B2 | DDC-B2-09 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
RF-8.RUN | Ventilation | RF-8 | Exhaust/supply fan | Serves AC-4 (B1F banquet lobby) | LCP-B2 | DDC-B2-09 | Run status | BI | DI dry contact | - |  |  | Y
RF-8.TRIP | Ventilation | RF-8 | Exhaust/supply fan | Serves AC-4 (B1F banquet lobby) | LCP-B2 | DDC-B2-09 | Fault | BI | DI dry contact | - |  | Y
RF-9.SS | Ventilation | RF-9 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-B2 | DDC-B2-09 | Start/Stop command | BO | DO relay | - | Y |  |  | Interlock w/ parent AHU
RF-9.RUN | Ventilation | RF-9 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-B2 | DDC-B2-09 | Run status | BI | DI dry contact | - |  |  | Y
RF-9.TRIP | Ventilation | RF-9 | Exhaust/supply fan | Serves AC-26 (Banquet-service office (B2F)) | LCP-B2 | DDC-B2-09 | Fault | BI | DI dry contact | - |  | Y
MTR-ELEC-MAIN | Metering | MTR-ELEC-MAIN | Energy meter | Whole building | LCP-B2 | DDC-B2-11 | Main electricity (kWh) | AI | Pulse/Modbus | kWh |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-GAS-MAIN | Metering | MTR-GAS-MAIN | Energy meter | Whole building | LCP-B2 | DDC-B2-11 | City gas (m³) | AI | Pulse/Modbus | m³ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-WATER-MAIN | Metering | MTR-WATER-MAIN | Energy meter | Whole building | LCP-B2 | DDC-B2-11 | City water (m³) | AI | Pulse/Modbus | m³ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-DHC-STEAM-L | Metering | MTR-DHC-STEAM-L | Energy meter | Whole building | LCP-B2 | DDC-B2-12 | DHC steam energy - low-rise | AI | Pulse/Modbus | GJ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-DHC-STEAM-H | Metering | MTR-DHC-STEAM-H | Energy meter | Whole building | LCP-PH | DDC-PH-20 | DHC steam energy - high-rise | AI | Pulse/Modbus | GJ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-DHC-CHW | Metering | MTR-DHC-CHW | Energy meter | Whole building | LCP-B2 | DDC-B2-12 | DHC chilled-water energy | AI | Pulse/Modbus | GJ |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-CHILLER-KWH | Metering | MTR-CHILLER-KWH | Energy meter | Whole building | LCP-PH | DDC-PH-20 | Chiller plant sub-meter | AI | Pulse/Modbus | kWh |  |  | Y | Integrating meter; thermal-demand & peak limiting
MTR-AHU-KWH | Metering | MTR-AHU-KWH | Energy meter | Whole building | LCP-B2 | DDC-B2-12 | AHU/OAU fans sub-meter | AI | Pulse/Modbus | kWh |  |  | Y | Integrating meter; thermal-demand & peak limiting
OA-STN.T | Common | OA-STN | Outdoor-air station | Rooftop | LCP-PH | DDC-PH-19 | Outdoor-air dry-bulb temp | AI | 4-20mA | °C |  |  | Y | Drives OA reset / economizer
OA-STN.RH | Common | OA-STN | Outdoor-air station | Rooftop | LCP-PH | DDC-PH-19 | Outdoor-air humidity | AI | 4-20mA | %RH |  |  | Y | Wet-bulb/enthalpy computed in BMS
POOL-FP.SS | Common | POOL-FP | Pool filtration pump | Pool plant | LCP-B2 | DDC-B2-10 | Start/Stop command | BO | DO relay | - | Y |  |  | Time schedule 8:00-19:00
POOL-FP.RUN | Common | POOL-FP | Pool filtration pump | Pool plant | LCP-B2 | DDC-B2-10 | Run status | BI | DI dry contact | -
POOL-FP.TRIP | Common | POOL-FP | Pool filtration pump | Pool plant | LCP-B2 | DDC-B2-10 | Fault | BI | DI dry contact | - |  | Y

## IO_Summary
System | AI | AO | BI | BO | Total
Heat source | 43 | 15 | 50 | 25 | 133
DHC interface | 18 | 4 | 4 | 6 | 32
Air side | 141 | 188 | 192 | 51 | 572
Ventilation | 2 | 2 | 72 | 36 | 112
Metering | 8 | 0 | 0 | 0 | 8
Common | 2 | 0 | 2 | 1 | 5
GRAND TOTAL | 214 | 209 | 320 | 119 | 862
Devices | 119
Panels | 7
Controllers | 52
Total I/O points | 862

## Legend
Abbreviation | Meaning
AI | Analog Input (sensor: temperature, humidity, pressure, flow, power, position fb)
AO | Analog Output (modulating command: valve %, damper %, VFD speed %)
BI | Binary Input (status / fault / proof dry contact)
BO | Binary Output (start/stop / open-close relay)
SP/Sched | Point carries a setpoint or time/seasonal/event schedule
CHW / CW | Chilled water / Condenser water
SAT / RAT | Supply-air temp / Return-air temp
CCV / HCV | Cooling-coil valve / Heating-coil (steam) valve
INV | Inverter / VFD fan speed control
Zero-energy band | Deadband between heating & cooling to prevent simultaneous operation
DHC | District Heating & Cooling (external steam / chilled supply)
HEX | Plate heat exchanger (DHC / secondary-loop hydraulic separator)
OAU (EVU) | Outdoor-air / make-up-air unit
INFERRED | Not explicitly confirmed in supplied docs — verify vs as-builts / Azbil 納入仕様書