## Summary
Red5-DHCP — Electrical / Power monitoring
BMS electrical cross-cut: energy meters, device kW power, and electrical-protection points.
Generated 2026-07-27 · source: generate_io_list.py
Panels | 7
Controllers | 26
Devices | 60
I/O points | 62
Panel | Description | Location | Ctrls | AI | AO | BI | BO | Points
LCP-DHC | DHC intake & hot-well panel | B2F Machine Room | 5 | 11 | 0 | 0 | 0 | 11
LCP-CT | Cooling-tower & condenser-water panel | Rooftop / PH | 4 | 1 | 0 | 7 | 0 | 8
LCP-HSL | Low-rise distribution panel (低層系統) | B2F Machine Room | 5 | 11 | 0 | 0 | 0 | 11
LCP-HSH | High-rise distribution panel (高層系統) | PH Machine Room | 5 | 10 | 3 | 0 | 0 | 13
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | 37F PH Machine Room | 4 | 8 | 1 | 1 | 0 | 10
LCP-4F | 4F–5F air-side panel | 4F AHU Room | 1 | 0 | 3 | 0 | 0 | 3
LCP-PKG | Packaged-unit & refrigeration panel | B3F–B1F EPS | 2 | 0 | 0 | 0 | 6 | 6
GRAND TOTAL |  |  | 26 | 41 | 7 | 8 | 6 | 62

## Pivot
Panel / Controller / Point | Description / devices | Device | I/O | System | Units
LCP-DHC | DHC intake & hot-well panel
DDC-DHC-01 | DHC-CHW
DHC-CHW.GJ | Thermal-energy meter | DHC-CHW | AI | DHC interface | GJ
DDC-DHC-04 | HP-5-1, HP-5-2, HP-3-1
HP-5-1.KW | Power | HP-5-1 | AI | Heat source | kW
HP-5-2.KW | Power | HP-5-2 | AI | Heat source | kW
HP-3-1.KW | Power | HP-3-1 | AI | Heat source | kW
DDC-DHC-05 | HP-3-2
HP-3-2.KW | Power | HP-3-2 | AI | Heat source | kW
DDC-DHC-06 | MTR-ELEC-MAIN, MTR-GAS-MAIN, MTR-WATER-MAIN
MTR-ELEC-MAIN | Main electricity (kWh) | MTR-ELEC-MAIN | AI | Metering | kWh
MTR-GAS-MAIN | City gas (m³) | MTR-GAS-MAIN | AI | Metering | m³
MTR-WATER-MAIN | City water (m³) | MTR-WATER-MAIN | AI | Metering | m³
DDC-DHC-07 | MTR-DHC-CHW, MTR-DHC-STEAM, MTR-DHC-COND
MTR-DHC-CHW | DHC chilled-water energy (受入) | MTR-DHC-CHW | AI | Metering | GJ
MTR-DHC-STEAM | DHC steam energy (受入) | MTR-DHC-STEAM | AI | Metering | t/h
MTR-DHC-COND | DHC condensate return (HR) | MTR-DHC-COND | AI | Metering | L
LCP-CT | Cooling-tower & condenser-water panel
DDC-CT-04 | CDP-1-1, CDP-1-2, CDP-1-3
CDP-1-1.TRIP | Fault / breaker trip | CDP-1-1 | BI | Condenser water | -
CDP-1-2.TRIP | Fault / breaker trip | CDP-1-2 | BI | Condenser water | -
CDP-1-3.TRIP | Fault / breaker trip | CDP-1-3 | BI | Condenser water | -
DDC-CT-05 | CDP-2-1, CDP-2-2, CDP-3-1
CDP-2-1.TRIP | Fault / breaker trip | CDP-2-1 | BI | Condenser water | -
CDP-2-2.TRIP | Fault / breaker trip | CDP-2-2 | BI | Condenser water | -
CDP-3-1.TRIP | Fault / breaker trip | CDP-3-1 | BI | Condenser water | -
DDC-CT-06 | CDP-3-2
CDP-3-2.TRIP | Fault / breaker trip | CDP-3-2 | BI | Condenser water | -
DDC-CT-08 | MTR-CDW-KWH
MTR-CDW-KWH | Cooling-tower/condenser sub-meter | MTR-CDW-KWH | AI | Metering | kWh
LCP-HSL | Low-rise distribution panel (低層系統)
DDC-HSL-02 | CP-1-1, CP-1-2, CP-1-3
CP-1-1.KW | Power | CP-1-1 | AI | Heat source | kW
CP-1-2.KW | Power | CP-1-2 | AI | Heat source | kW
CP-1-3.KW | Power | CP-1-3 | AI | Heat source | kW
DDC-HSL-03 | CP-4-1, CP-4-2, CP-5-1
CP-4-1.KW | Power | CP-4-1 | AI | Heat source | kW
CP-4-2.KW | Power | CP-4-2 | AI | Heat source | kW
CP-5-1.KW | Power | CP-5-1 | AI | Heat source | kW
DDC-HSL-04 | CP-5-2
CP-5-2.KW | Power | CP-5-2 | AI | Heat source | kW
DDC-HSL-05 | HP-1-1, HP-1-2, HP-1-3
HP-1-1.KW | Power | HP-1-1 | AI | Heat source | kW
HP-1-2.KW | Power | HP-1-2 | AI | Heat source | kW
HP-1-3.KW | Power | HP-1-3 | AI | Heat source | kW
DDC-HSL-17 | MTR-AHU-KWH
MTR-AHU-KWH | AHU/OAU fans sub-meter | MTR-AHU-KWH | AI | Metering | kWh
LCP-HSH | High-rise distribution panel (高層系統)
DDC-HSH-02 | CP-2-1, CP-2-2, CP-2-3
CP-2-1.KW | Power | CP-2-1 | AI | Heat source | kW
CP-2-2.KW | Power | CP-2-2 | AI | Heat source | kW
CP-2-3.KW | Power | CP-2-3 | AI | Heat source | kW
DDC-HSH-03 | CP-3-1, CP-3-2, CP-6-1
CP-3-1.KW | Power | CP-3-1 | AI | Heat source | kW
CP-3-2.KW | Power | CP-3-2 | AI | Heat source | kW
CP-6-1.KW | Power | CP-6-1 | AI | Heat source | kW
DDC-HSH-04 | CP-6-2
CP-6-2.KW | Power | CP-6-2 | AI | Heat source | kW
DDC-HSH-05 | HP-2-1, HP-2-2, HP-2-3
HP-2-1.KW | Power | HP-2-1 | AI | Heat source | kW
HP-2-2.KW | Power | HP-2-2 | AI | Heat source | kW
HP-2-3.KW | Power | HP-2-3 | AI | Heat source | kW
DDC-HSH-08 | EVU-11, EVU-12, EVU-13
EVU-11.SPD | Supply fan VFD (INV) speed | EVU-11 | AO | Air side | %
EVU-12.SPD | Supply fan VFD (INV) speed | EVU-12 | AO | Air side | %
EVU-13.SPD | Supply fan VFD (INV) speed | EVU-13 | AO | Air side | %
LCP-3637 | 36/37F local heat-source panel (36,37F系統)
DDC-3637-01 | R-1
R-1.TRIP | Common fault / trip | R-1 | BI | Heat source | -
R-1.DMD | Capacity/demand limit | R-1 | AO | Heat source | %
R-1.KW | Electrical input power | R-1 | AI | Heat source | kW
DDC-3637-03 | CP-7-1, CP-7-2, CP-8-1
CP-7-1.KW | Power | CP-7-1 | AI | Heat source | kW
CP-7-2.KW | Power | CP-7-2 | AI | Heat source | kW
CP-8-1.KW | Power | CP-8-1 | AI | Heat source | kW
DDC-3637-04 | CP-8-2, CP-8-3
CP-8-2.KW | Power | CP-8-2 | AI | Heat source | kW
CP-8-3.KW | Power | CP-8-3 | AI | Heat source | kW
DDC-3637-05 | HP-4-1, HP-4-2
HP-4-1.KW | Power | HP-4-1 | AI | Heat source | kW
HP-4-2.KW | Power | HP-4-2 | AI | Heat source | kW
LCP-4F | 4F–5F air-side panel
DDC-4F-03 | EVU-8, EVU-9, EVU-10
EVU-8.SPD | Supply fan VFD (INV) speed | EVU-8 | AO | Air side | %
EVU-9.SPD | Supply fan VFD (INV) speed | EVU-9 | AO | Air side | %
EVU-10.SPD | Supply fan VFD (INV) speed | EVU-10 | AO | Air side | %
LCP-PKG | Packaged-unit & refrigeration panel
DDC-PKG-01 | PAC-1-1, PAC-1-2, PAC-2
PAC-1-1.SS | Start/Stop command | PAC-1-1 | BO | Packaged units | -
PAC-1-2.SS | Start/Stop command | PAC-1-2 | BO | Packaged units | -
PAC-2.SS | Start/Stop command | PAC-2 | BO | Packaged units | -
DDC-PKG-02 | PAC-3, PAC-4, PAC-5
PAC-3.SS | Start/Stop command | PAC-3 | BO | Packaged units | -
PAC-4.SS | Start/Stop command | PAC-4 | BO | Packaged units | -
PAC-5.SS | Start/Stop command | PAC-5 | BO | Packaged units | -

## Flat
Panel | Panel description | Controller | Device ID | Point Tag | I/O | System | Units | Description | Notes / Basis
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.GJ | AI | DHC interface | GJ | Thermal-energy meter | GJ/h + integrated; thermal-demand control
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-06 | MTR-ELEC-MAIN | MTR-ELEC-MAIN | AI | Metering | kWh | Main electricity (kWh) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-06 | MTR-GAS-MAIN | MTR-GAS-MAIN | AI | Metering | m³ | City gas (m³) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-06 | MTR-WATER-MAIN | MTR-WATER-MAIN | AI | Metering | m³ | City water (m³) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-07 | MTR-DHC-CHW | MTR-DHC-CHW | AI | Metering | GJ | DHC chilled-water energy (受入) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-07 | MTR-DHC-STEAM | MTR-DHC-STEAM | AI | Metering | t/h | DHC steam energy (受入) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-07 | MTR-DHC-COND | MTR-DHC-COND | AI | Metering | L | DHC condensate return (HR) | Integrating meter; thermal-demand & peak limiting
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-1 | CDP-1-1.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-2 | CDP-1-2.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-3 | CDP-1-3.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-1 | CDP-2-1.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-2 | CDP-2-2.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-3-1 | CDP-3-1.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-06 | CDP-3-2 | CDP-3-2.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-08 | MTR-CDW-KWH | MTR-CDW-KWH | AI | Metering | kWh | Cooling-tower/condenser sub-meter | Integrating meter; thermal-demand & peak limiting
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-17 | MTR-AHU-KWH | MTR-AHU-KWH | AI | Metering | kWh | AHU/OAU fans sub-meter | Integrating meter; thermal-demand & peak limiting
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.TRIP | BI | Heat source | - | Common fault / trip
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.DMD | AO | Heat source | % | Capacity/demand limit | Demand-limit / soft-load
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.KW | AI | Heat source | kW | Electrical input power | Ebara screw RHS DW202M2: 370 kW cool / 82.2 kW in (COP 4.5); 2×45 kW screw comp, R-407C
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.KW | AI | Heat source | kW | Power
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-1 | PAC-1-1.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-2 | PAC-1-2.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-2 | PAC-2.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-3 | PAC-3.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-4 | PAC-4.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-5 | PAC-5.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)