## Summary
Red5-DHCP — Full BMS I/O
Every DDC panel → controller → point in the savic-net FX2 model.
Generated 2026-07-27 · source: generate_io_list.py
Panels | 11
Controllers | 84
Devices | 190
I/O points | 1160
Panel | Description | Location | Ctrls | AI | AO | BI | BO | Points
LCP-DHC | DHC intake & hot-well panel | B2F Machine Room | 7 | 27 | 6 | 16 | 7 | 56
LCP-CT | Cooling-tower & condenser-water panel | Rooftop / PH | 8 | 12 | 6 | 38 | 27 | 83
LCP-HSL | Low-rise distribution panel (低層系統) | B2F Machine Room | 17 | 54 | 47 | 90 | 31 | 222
LCP-HSH | High-rise distribution panel (高層系統) | PH Machine Room | 11 | 53 | 42 | 67 | 20 | 182
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | 37F PH Machine Room | 13 | 47 | 35 | 66 | 23 | 171
LCP-1F | 1F–2F air-side panel | 1F EPS/AHU Room | 3 | 12 | 16 | 20 | 6 | 54
LCP-2F | 2F air-side panel | 2F AHU Room | 4 | 26 | 37 | 42 | 12 | 117
LCP-3F | 3F air-side panel | 3F AHU Room | 4 | 13 | 17 | 28 | 10 | 68
LCP-4F | 4F–5F air-side panel | 4F AHU Room | 7 | 29 | 34 | 52 | 18 | 133
LCP-PKG | Packaged-unit & refrigeration panel | B3F–B1F EPS | 7 | 0 | 0 | 41 | 17 | 58
LCP-LTG | Common-area & facade lighting panel | Distributed EPS | 3 | 0 | 0 | 8 | 8 | 16
GRAND TOTAL |  |  | 84 | 273 | 240 | 468 | 179 | 1160

## Pivot
Panel / Controller / Point | Description / devices | Device | I/O | System | Units
LCP-DHC | DHC intake & hot-well panel
DDC-DHC-01 | DHC-CHW
DHC-CHW.CS-T | Supply (CS) temp | DHC-CHW | AI | DHC interface | °C
DHC-CHW.CR-T | Return (CR) temp | DHC-CHW | AI | DHC interface | °C
DHC-CHW.CS-P | Supply header pressure | DHC-CHW | AI | DHC interface | MPa
DHC-CHW.CR-P | Return header pressure | DHC-CHW | AI | DHC interface | MPa
DHC-CHW.FLW | Intake flow | DHC-CHW | AI | DHC interface | m³/h
DHC-CHW.GJ | Thermal-energy meter | DHC-CHW | AI | DHC interface | GJ
DHC-CHW.CV | Intake control valve | DHC-CHW | AO | DHC interface | %
DHC-CHW.CVFB | Intake valve position fb | DHC-CHW | AI | DHC interface | %
DHC-CHW.ISOL | Intake isolation valve open/close | DHC-CHW | BO | DHC interface | -
DHC-CHW.ISOL-ST | Isolation valve status | DHC-CHW | BI | DHC interface | -
DDC-DHC-02 | DHC-STEAM
DHC-STEAM.SS-P | Supply (SS 8k) pressure | DHC-STEAM | AI | DHC interface | MPa
DHC-STEAM.MASS | Steam mass-flow meter | DHC-STEAM | AI | DHC interface | t/h
DHC-STEAM.PRV | PRV 8k->2k reducing valve | DHC-STEAM | AO | DHC interface | %
DHC-STEAM.SSH2-P | Reduced (SSH 2k) pressure | DHC-STEAM | AI | DHC interface | MPa
DHC-STEAM.ISOL | Main isolation valve open/close | DHC-STEAM | BO | DHC interface | -
DHC-STEAM.ISOL-ST | Isolation valve status | DHC-STEAM | BI | DHC interface | -
DHC-STEAM.HR-M | Condensate (HR) return meter | DHC-STEAM | AI | DHC interface | L
DDC-DHC-03 | HWT-1
HWT-1.LVL | Tank level | HWT-1 | AI | Heat source | %
HWT-1.HI | High-level alarm | HWT-1 | BI | Heat source | -
HWT-1.LO | Low-level alarm | HWT-1 | BI | Heat source | -
HWT-1.T | Condensate temp | HWT-1 | AI | Heat source | °C
HWT-1.MU | Make-up water valve | HWT-1 | BO | Heat source | -
DDC-DHC-04 | HP-5-1, HP-5-2, HP-3-1
HP-5-1.RUN | Run status | HP-5-1 | BI | Heat source | -
HP-5-1.TRIP | VFD/pump fault | HP-5-1 | BI | Heat source | -
HP-5-1.SS | Start/Stop command | HP-5-1 | BO | Heat source | -
HP-5-1.SPD | VFD speed command | HP-5-1 | AO | Heat source | %
HP-5-1.SPDFB | VFD speed feedback | HP-5-1 | AI | Heat source | %
HP-5-1.KW | Power | HP-5-1 | AI | Heat source | kW
HP-5-1.FLW | Flow/DP proof | HP-5-1 | BI | Heat source | -
HP-5-2.RUN | Run status | HP-5-2 | BI | Heat source | -
HP-5-2.TRIP | VFD/pump fault | HP-5-2 | BI | Heat source | -
HP-5-2.SS | Start/Stop command | HP-5-2 | BO | Heat source | -
HP-5-2.SPD | VFD speed command | HP-5-2 | AO | Heat source | %
HP-5-2.SPDFB | VFD speed feedback | HP-5-2 | AI | Heat source | %
HP-5-2.KW | Power | HP-5-2 | AI | Heat source | kW
HP-5-2.FLW | Flow/DP proof | HP-5-2 | BI | Heat source | -
HP-3-1.RUN | Run status | HP-3-1 | BI | Heat source | -
HP-3-1.TRIP | VFD/pump fault | HP-3-1 | BI | Heat source | -
HP-3-1.SS | Start/Stop command | HP-3-1 | BO | Heat source | -
HP-3-1.SPD | VFD speed command | HP-3-1 | AO | Heat source | %
HP-3-1.SPDFB | VFD speed feedback | HP-3-1 | AI | Heat source | %
HP-3-1.KW | Power | HP-3-1 | AI | Heat source | kW
HP-3-1.FLW | Flow/DP proof | HP-3-1 | BI | Heat source | -
DDC-DHC-05 | HP-3-2
HP-3-2.RUN | Run status | HP-3-2 | BI | Heat source | -
HP-3-2.TRIP | VFD/pump fault | HP-3-2 | BI | Heat source | -
HP-3-2.SS | Start/Stop command | HP-3-2 | BO | Heat source | -
HP-3-2.SPD | VFD speed command | HP-3-2 | AO | Heat source | %
HP-3-2.SPDFB | VFD speed feedback | HP-3-2 | AI | Heat source | %
HP-3-2.KW | Power | HP-3-2 | AI | Heat source | kW
HP-3-2.FLW | Flow/DP proof | HP-3-2 | BI | Heat source | -
DDC-DHC-06 | MTR-ELEC-MAIN, MTR-GAS-MAIN, MTR-WATER-MAIN
MTR-ELEC-MAIN | Main electricity (kWh) | MTR-ELEC-MAIN | AI | Metering | kWh
MTR-GAS-MAIN | City gas (m³) | MTR-GAS-MAIN | AI | Metering | m³
MTR-WATER-MAIN | City water (m³) | MTR-WATER-MAIN | AI | Metering | m³
DDC-DHC-07 | MTR-DHC-CHW, MTR-DHC-STEAM, MTR-DHC-COND
MTR-DHC-CHW | DHC chilled-water energy (受入) | MTR-DHC-CHW | AI | Metering | GJ
MTR-DHC-STEAM | DHC steam energy (受入) | MTR-DHC-STEAM | AI | Metering | t/h
MTR-DHC-COND | DHC condensate return (HR) | MTR-DHC-COND | AI | Metering | L
LCP-CT | Cooling-tower & condenser-water panel
DDC-CT-01 | CT-1-1, CT-1-2, CT-1
CT-1-1.RUN | Fan run status | CT-1-1 | BI | Condenser water | -
CT-1-1.TRIP | Fan INV fault | CT-1-1 | BI | Condenser water | -
CT-1-1.SS | Fan start/stop | CT-1-1 | BO | Condenser water | -
CT-1-1.SPD | Fan VFD speed command | CT-1-1 | AO | Condenser water | %
CT-1-1.SPDFB | Fan speed feedback | CT-1-1 | AI | Condenser water | %
CT-1-2.RUN | Fan run status | CT-1-2 | BI | Condenser water | -
CT-1-2.TRIP | Fan INV fault | CT-1-2 | BI | Condenser water | -
CT-1-2.SS | Fan start/stop | CT-1-2 | BO | Condenser water | -
CT-1-2.SPD | Fan VFD speed command | CT-1-2 | AO | Condenser water | %
CT-1-2.SPDFB | Fan speed feedback | CT-1-2 | AI | Condenser water | %
CT-1.LVL | Basin water level | CT-1 | AI | Condenser water | %
CT-1.MU | Make-up water valve | CT-1 | BO | Condenser water | -
CT-1.BLD | Bleed/blowdown valve | CT-1 | BO | Condenser water | -
CT-1.DRY | Low-water (渇水) alarm | CT-1 | BI | Condenser water | -
CT-1.CHEM | Chemical dosing (薬注) batch fault | CT-1 | BI | Condenser water | -
CT-1.EH | Basin heater (E/H) enable | CT-1 | BO | Condenser water | -
DDC-CT-02 | CT-2-1, CT-2-2, CT-2
CT-2-1.RUN | Fan run status | CT-2-1 | BI | Condenser water | -
CT-2-1.TRIP | Fan INV fault | CT-2-1 | BI | Condenser water | -
CT-2-1.SS | Fan start/stop | CT-2-1 | BO | Condenser water | -
CT-2-1.SPD | Fan VFD speed command | CT-2-1 | AO | Condenser water | %
CT-2-1.SPDFB | Fan speed feedback | CT-2-1 | AI | Condenser water | %
CT-2-2.RUN | Fan run status | CT-2-2 | BI | Condenser water | -
CT-2-2.TRIP | Fan INV fault | CT-2-2 | BI | Condenser water | -
CT-2-2.SS | Fan start/stop | CT-2-2 | BO | Condenser water | -
CT-2-2.SPD | Fan VFD speed command | CT-2-2 | AO | Condenser water | %
CT-2-2.SPDFB | Fan speed feedback | CT-2-2 | AI | Condenser water | %
CT-2.LVL | Basin water level | CT-2 | AI | Condenser water | %
CT-2.MU | Make-up water valve | CT-2 | BO | Condenser water | -
CT-2.BLD | Bleed/blowdown valve | CT-2 | BO | Condenser water | -
CT-2.DRY | Low-water (渇水) alarm | CT-2 | BI | Condenser water | -
CT-2.CHEM | Chemical dosing (薬注) batch fault | CT-2 | BI | Condenser water | -
CT-2.EH | Basin heater (E/H) enable | CT-2 | BO | Condenser water | -
CT-2.FILT-RUN | Filtration (ろ過) pump run | CT-2 | BI | Condenser water | -
CT-2.FILT-SS | Filtration pump start/stop | CT-2 | BO | Condenser water | -
DDC-CT-03 | CT-3-1, CT-3
CT-3-1.RUN | Fan run status | CT-3-1 | BI | Condenser water | -
CT-3-1.TRIP | Fan INV fault | CT-3-1 | BI | Condenser water | -
CT-3-1.SS | Fan start/stop | CT-3-1 | BO | Condenser water | -
CT-3-1.SPD | Fan VFD speed command | CT-3-1 | AO | Condenser water | %
CT-3-1.SPDFB | Fan speed feedback | CT-3-1 | AI | Condenser water | %
CT-3.LVL | Basin water level | CT-3 | AI | Condenser water | %
CT-3.MU | Make-up water valve | CT-3 | BO | Condenser water | -
CT-3.BLD | Bleed/blowdown valve | CT-3 | BO | Condenser water | -
CT-3.DRY | Low-water (渇水) alarm | CT-3 | BI | Condenser water | -
CT-3.CHEM | Chemical dosing (薬注) batch fault | CT-3 | BI | Condenser water | -
CT-3.EH | Basin heater (E/H) enable | CT-3 | BO | Condenser water | -
DDC-CT-04 | CDP-1-1, CDP-1-2, CDP-1-3
CDP-1-1.RUN | Run status | CDP-1-1 | BI | Condenser water | -
CDP-1-1.TRIP | Fault / breaker trip | CDP-1-1 | BI | Condenser water | -
CDP-1-1.SS | Start/Stop command | CDP-1-1 | BO | Condenser water | -
CDP-1-1.FLW | Flow/DP proof | CDP-1-1 | BI | Condenser water | -
CDP-1-2.RUN | Run status | CDP-1-2 | BI | Condenser water | -
CDP-1-2.TRIP | Fault / breaker trip | CDP-1-2 | BI | Condenser water | -
CDP-1-2.SS | Start/Stop command | CDP-1-2 | BO | Condenser water | -
CDP-1-2.FLW | Flow/DP proof | CDP-1-2 | BI | Condenser water | -
CDP-1-3.RUN | Run status | CDP-1-3 | BI | Condenser water | -
CDP-1-3.TRIP | Fault / breaker trip | CDP-1-3 | BI | Condenser water | -
CDP-1-3.SS | Start/Stop command | CDP-1-3 | BO | Condenser water | -
CDP-1-3.FLW | Flow/DP proof | CDP-1-3 | BI | Condenser water | -
DDC-CT-05 | CDP-2-1, CDP-2-2, CDP-3-1
CDP-2-1.RUN | Run status | CDP-2-1 | BI | Condenser water | -
CDP-2-1.TRIP | Fault / breaker trip | CDP-2-1 | BI | Condenser water | -
CDP-2-1.SS | Start/Stop command | CDP-2-1 | BO | Condenser water | -
CDP-2-1.FLW | Flow/DP proof | CDP-2-1 | BI | Condenser water | -
CDP-2-2.RUN | Run status | CDP-2-2 | BI | Condenser water | -
CDP-2-2.TRIP | Fault / breaker trip | CDP-2-2 | BI | Condenser water | -
CDP-2-2.SS | Start/Stop command | CDP-2-2 | BO | Condenser water | -
CDP-2-2.FLW | Flow/DP proof | CDP-2-2 | BI | Condenser water | -
CDP-3-1.RUN | Run status | CDP-3-1 | BI | Condenser water | -
CDP-3-1.TRIP | Fault / breaker trip | CDP-3-1 | BI | Condenser water | -
CDP-3-1.SS | Start/Stop command | CDP-3-1 | BO | Condenser water | -
CDP-3-1.FLW | Flow/DP proof | CDP-3-1 | BI | Condenser water | -
DDC-CT-06 | CDP-3-2
CDP-3-2.RUN | Run status | CDP-3-2 | BI | Condenser water | -
CDP-3-2.TRIP | Fault / breaker trip | CDP-3-2 | BI | Condenser water | -
CDP-3-2.SS | Start/Stop command | CDP-3-2 | BO | Condenser water | -
CDP-3-2.FLW | Flow/DP proof | CDP-3-2 | BI | Condenser water | -
DDC-CT-07 | EX-1, EMHX-1, EMHX-2
EX-1.EN | Free-cooling enable / changeover | EX-1 | BO | Condenser water | -
EX-1.ST | CHW-side leaving temp | EX-1 | AI | Condenser water | °C
EX-1.CV | CW-side control valve | EX-1 | AO | Condenser water | %
EMHX-1.EN | Emergency cooling enable | EMHX-1 | BO | Condenser water | -
EMHX-1.ST | Cooling-water leaving temp | EMHX-1 | AI | Condenser water | °C
EMHX-1.ISOL | DHC-side isolation valve | EMHX-1 | BO | Condenser water | -
EMHX-2.EN | Emergency cooling enable | EMHX-2 | BO | Condenser water | -
EMHX-2.ST | Cooling-water leaving temp | EMHX-2 | AI | Condenser water | °C
EMHX-2.ISOL | DHC-side isolation valve | EMHX-2 | BO | Condenser water | -
DDC-CT-08 | MTR-CDW-KWH
MTR-CDW-KWH | Cooling-tower/condenser sub-meter | MTR-CDW-KWH | AI | Metering | kWh
LCP-HSL | Low-rise distribution panel (低層系統)
DDC-HSL-01 | EX-2-1, EX-2-2
EX-2-1.P-IN | Primary inlet temp (laundry) | EX-2-1 | AI | Heat source | °C
EX-2-1.S-OUT | Secondary outlet (supply) temp | EX-2-1 | AI | Heat source | °C
EX-2-1.PV | Primary control valve | EX-2-1 | AO | Heat source | %
EX-2-1.PVFB | Primary valve position fb | EX-2-1 | AI | Heat source | %
EX-2-2.P-IN | Primary inlet temp (laundry) | EX-2-2 | AI | Heat source | °C
EX-2-2.S-OUT | Secondary outlet (supply) temp | EX-2-2 | AI | Heat source | °C
EX-2-2.PV | Primary control valve | EX-2-2 | AO | Heat source | %
EX-2-2.PVFB | Primary valve position fb | EX-2-2 | AI | Heat source | %
DDC-HSL-02 | CP-1-1, CP-1-2, CP-1-3
CP-1-1.RUN | Run status | CP-1-1 | BI | Heat source | -
CP-1-1.TRIP | VFD/pump fault | CP-1-1 | BI | Heat source | -
CP-1-1.SS | Start/Stop command | CP-1-1 | BO | Heat source | -
CP-1-1.SPD | VFD speed command | CP-1-1 | AO | Heat source | %
CP-1-1.SPDFB | VFD speed feedback | CP-1-1 | AI | Heat source | %
CP-1-1.KW | Power | CP-1-1 | AI | Heat source | kW
CP-1-1.FLW | Flow/DP proof | CP-1-1 | BI | Heat source | -
CP-1-2.RUN | Run status | CP-1-2 | BI | Heat source | -
CP-1-2.TRIP | VFD/pump fault | CP-1-2 | BI | Heat source | -
CP-1-2.SS | Start/Stop command | CP-1-2 | BO | Heat source | -
CP-1-2.SPD | VFD speed command | CP-1-2 | AO | Heat source | %
CP-1-2.SPDFB | VFD speed feedback | CP-1-2 | AI | Heat source | %
CP-1-2.KW | Power | CP-1-2 | AI | Heat source | kW
CP-1-2.FLW | Flow/DP proof | CP-1-2 | BI | Heat source | -
CP-1-3.RUN | Run status | CP-1-3 | BI | Heat source | -
CP-1-3.TRIP | VFD/pump fault | CP-1-3 | BI | Heat source | -
CP-1-3.SS | Start/Stop command | CP-1-3 | BO | Heat source | -
CP-1-3.SPD | VFD speed command | CP-1-3 | AO | Heat source | %
CP-1-3.SPDFB | VFD speed feedback | CP-1-3 | AI | Heat source | %
CP-1-3.KW | Power | CP-1-3 | AI | Heat source | kW
CP-1-3.FLW | Flow/DP proof | CP-1-3 | BI | Heat source | -
DDC-HSL-03 | CP-4-1, CP-4-2, CP-5-1
CP-4-1.RUN | Run status | CP-4-1 | BI | Heat source | -
CP-4-1.TRIP | VFD/pump fault | CP-4-1 | BI | Heat source | -
CP-4-1.SS | Start/Stop command | CP-4-1 | BO | Heat source | -
CP-4-1.SPD | VFD speed command | CP-4-1 | AO | Heat source | %
CP-4-1.SPDFB | VFD speed feedback | CP-4-1 | AI | Heat source | %
CP-4-1.KW | Power | CP-4-1 | AI | Heat source | kW
CP-4-1.FLW | Flow/DP proof | CP-4-1 | BI | Heat source | -
CP-4-2.RUN | Run status | CP-4-2 | BI | Heat source | -
CP-4-2.TRIP | VFD/pump fault | CP-4-2 | BI | Heat source | -
CP-4-2.SS | Start/Stop command | CP-4-2 | BO | Heat source | -
CP-4-2.SPD | VFD speed command | CP-4-2 | AO | Heat source | %
CP-4-2.SPDFB | VFD speed feedback | CP-4-2 | AI | Heat source | %
CP-4-2.KW | Power | CP-4-2 | AI | Heat source | kW
CP-4-2.FLW | Flow/DP proof | CP-4-2 | BI | Heat source | -
CP-5-1.RUN | Run status | CP-5-1 | BI | Heat source | -
CP-5-1.TRIP | VFD/pump fault | CP-5-1 | BI | Heat source | -
CP-5-1.SS | Start/Stop command | CP-5-1 | BO | Heat source | -
CP-5-1.SPD | VFD speed command | CP-5-1 | AO | Heat source | %
CP-5-1.SPDFB | VFD speed feedback | CP-5-1 | AI | Heat source | %
CP-5-1.KW | Power | CP-5-1 | AI | Heat source | kW
CP-5-1.FLW | Flow/DP proof | CP-5-1 | BI | Heat source | -
DDC-HSL-04 | CP-5-2
CP-5-2.RUN | Run status | CP-5-2 | BI | Heat source | -
CP-5-2.TRIP | VFD/pump fault | CP-5-2 | BI | Heat source | -
CP-5-2.SS | Start/Stop command | CP-5-2 | BO | Heat source | -
CP-5-2.SPD | VFD speed command | CP-5-2 | AO | Heat source | %
CP-5-2.SPDFB | VFD speed feedback | CP-5-2 | AI | Heat source | %
CP-5-2.KW | Power | CP-5-2 | AI | Heat source | kW
CP-5-2.FLW | Flow/DP proof | CP-5-2 | BI | Heat source | -
DDC-HSL-05 | HP-1-1, HP-1-2, HP-1-3
HP-1-1.RUN | Run status | HP-1-1 | BI | Heat source | -
HP-1-1.TRIP | VFD/pump fault | HP-1-1 | BI | Heat source | -
HP-1-1.SS | Start/Stop command | HP-1-1 | BO | Heat source | -
HP-1-1.SPD | VFD speed command | HP-1-1 | AO | Heat source | %
HP-1-1.SPDFB | VFD speed feedback | HP-1-1 | AI | Heat source | %
HP-1-1.KW | Power | HP-1-1 | AI | Heat source | kW
HP-1-1.FLW | Flow/DP proof | HP-1-1 | BI | Heat source | -
HP-1-2.RUN | Run status | HP-1-2 | BI | Heat source | -
HP-1-2.TRIP | VFD/pump fault | HP-1-2 | BI | Heat source | -
HP-1-2.SS | Start/Stop command | HP-1-2 | BO | Heat source | -
HP-1-2.SPD | VFD speed command | HP-1-2 | AO | Heat source | %
HP-1-2.SPDFB | VFD speed feedback | HP-1-2 | AI | Heat source | %
HP-1-2.KW | Power | HP-1-2 | AI | Heat source | kW
HP-1-2.FLW | Flow/DP proof | HP-1-2 | BI | Heat source | -
HP-1-3.RUN | Run status | HP-1-3 | BI | Heat source | -
HP-1-3.TRIP | VFD/pump fault | HP-1-3 | BI | Heat source | -
HP-1-3.SS | Start/Stop command | HP-1-3 | BO | Heat source | -
HP-1-3.SPD | VFD speed command | HP-1-3 | AO | Heat source | %
HP-1-3.SPDFB | VFD speed feedback | HP-1-3 | AI | Heat source | %
HP-1-3.KW | Power | HP-1-3 | AI | Heat source | kW
HP-1-3.FLW | Flow/DP proof | HP-1-3 | BI | Heat source | -
DDC-HSL-06 | EXT-1
EXT-1.LVL | Tank level | EXT-1 | AI | Heat source | %
EXT-1.HI | High-level alarm | EXT-1 | BI | Heat source | -
EXT-1.LO | Low-level alarm | EXT-1 | BI | Heat source | -
DDC-HSL-07 | ST-1
ST-1.T | Outdoor dry-bulb temp | ST-1 | AI | Common | °C
ST-1.RH | Outdoor humidity | ST-1 | AI | Common | %RH
ST-1.WB | Wet-bulb temp (計測/演算) | ST-1 | AI | Common | °C
DDC-HSL-08 | AC-1, AC-2, AC-3
AC-1.RUN | Supply fan run status | AC-1 | BI | Air side | -
AC-1.TRIP | Supply fan fault | AC-1 | BI | Air side | -
AC-1.SS | Supply fan start/stop | AC-1 | BO | Air side | -
AC-1.SPD | Supply fan speed (fixed) | AC-1 | AO | Air side | %
AC-1.SAT | Supply air temp | AC-1 | AI | Air side | °C
AC-1.RAT | Return air temp | AC-1 | AI | Air side | °C
AC-1.CCV | Cooling coil (CHW) valve | AC-1 | AO | Air side | %
AC-1.HCV | Heating coil (steam) valve | AC-1 | AO | Air side | %
AC-1.FLT | Filter dirty (DP) | AC-1 | BI | Air side | -
AC-1.OAD | Outdoor-air damper | AC-1 | AO | Air side | %
AC-1.FRZ | Freeze protection stat | AC-1 | BI | Air side | -
AC-2.RUN | Supply fan run status | AC-2 | BI | Air side | -
AC-2.TRIP | Supply fan fault | AC-2 | BI | Air side | -
AC-2.SS | Supply fan start/stop | AC-2 | BO | Air side | -
AC-2.SPD | Supply fan speed (fixed) | AC-2 | AO | Air side | %
AC-2.SAT | Supply air temp | AC-2 | AI | Air side | °C
AC-2.RAT | Return air temp | AC-2 | AI | Air side | °C
AC-2.CCV | Cooling coil (CHW) valve | AC-2 | AO | Air side | %
AC-2.FLT | Filter dirty (DP) | AC-2 | BI | Air side | -
AC-2.OAD | Outdoor-air damper | AC-2 | AO | Air side | %
AC-3.RUN | Supply fan run status | AC-3 | BI | Air side | -
AC-3.TRIP | Supply fan fault | AC-3 | BI | Air side | -
AC-3.SS | Supply fan start/stop | AC-3 | BO | Air side | -
AC-3.SPD | Supply fan speed (fixed) | AC-3 | AO | Air side | %
AC-3.SAT | Supply air temp | AC-3 | AI | Air side | °C
AC-3.RAT | Return air temp | AC-3 | AI | Air side | °C
AC-3.CCV | Cooling coil (CHW) valve | AC-3 | AO | Air side | %
AC-3.FLT | Filter dirty (DP) | AC-3 | BI | Air side | -
AC-3.OAD | Outdoor-air damper | AC-3 | AO | Air side | %
DDC-HSL-09 | AC-4, AC-5, AC-6
AC-4.RUN | Supply fan run status | AC-4 | BI | Air side | -
AC-4.TRIP | Supply fan fault | AC-4 | BI | Air side | -
AC-4.SS | Supply fan start/stop | AC-4 | BO | Air side | -
AC-4.SPD | Supply fan VFD (INV) speed | AC-4 | AO | Air side | %
AC-4.SPDFB | Supply fan speed feedback | AC-4 | AI | Air side | %
AC-4.SAT | Supply air temp | AC-4 | AI | Air side | °C
AC-4.RAT | Return air temp | AC-4 | AI | Air side | °C
AC-4.CCV | Cooling coil (CHW) valve | AC-4 | AO | Air side | %
AC-4.FLT | Filter dirty (DP) | AC-4 | BI | Air side | -
AC-4.OAD | Outdoor-air damper | AC-4 | AO | Air side | %
AC-5.RUN | Supply fan run status | AC-5 | BI | Air side | -
AC-5.TRIP | Supply fan fault | AC-5 | BI | Air side | -
AC-5.SS | Supply fan start/stop | AC-5 | BO | Air side | -
AC-5.SPD | Supply fan VFD (INV) speed | AC-5 | AO | Air side | %
AC-5.SPDFB | Supply fan speed feedback | AC-5 | AI | Air side | %
AC-5.SAT | Supply air temp | AC-5 | AI | Air side | °C
AC-5.RAT | Return air temp | AC-5 | AI | Air side | °C
AC-5.CCV | Cooling coil (CHW) valve | AC-5 | AO | Air side | %
AC-5.HCV | Heating coil (steam) valve | AC-5 | AO | Air side | %
AC-5.FLT | Filter dirty (DP) | AC-5 | BI | Air side | -
AC-5.OAD | Outdoor-air damper | AC-5 | AO | Air side | %
AC-5.FRZ | Freeze protection stat | AC-5 | BI | Air side | -
AC-6.RUN | Supply fan run status | AC-6 | BI | Air side | -
AC-6.TRIP | Supply fan fault | AC-6 | BI | Air side | -
AC-6.SS | Supply fan start/stop | AC-6 | BO | Air side | -
AC-6.SPD | Supply fan VFD (INV) speed | AC-6 | AO | Air side | %
AC-6.SPDFB | Supply fan speed feedback | AC-6 | AI | Air side | %
AC-6.SAT | Supply air temp | AC-6 | AI | Air side | °C
AC-6.RAT | Return air temp | AC-6 | AI | Air side | °C
AC-6.CCV | Cooling coil (CHW) valve | AC-6 | AO | Air side | %
AC-6.HCV | Heating coil (steam) valve | AC-6 | AO | Air side | %
AC-6.FLT | Filter dirty (DP) | AC-6 | BI | Air side | -
AC-6.OAD | Outdoor-air damper | AC-6 | AO | Air side | %
AC-6.FRZ | Freeze protection stat | AC-6 | BI | Air side | -
DDC-HSL-10 | AC-26
AC-26.RUN | Supply fan run status | AC-26 | BI | Air side | -
AC-26.TRIP | Supply fan fault | AC-26 | BI | Air side | -
AC-26.SS | Supply fan start/stop | AC-26 | BO | Air side | -
AC-26.SPD | Supply fan VFD (INV) speed | AC-26 | AO | Air side | %
AC-26.SPDFB | Supply fan speed feedback | AC-26 | AI | Air side | %
AC-26.SAT | Supply air temp | AC-26 | AI | Air side | °C
AC-26.RAT | Return air temp | AC-26 | AI | Air side | °C
AC-26.CCV | Cooling coil (CHW) valve | AC-26 | AO | Air side | %
AC-26.HCV | Heating coil (steam) valve | AC-26 | AO | Air side | %
AC-26.FLT | Filter dirty (DP) | AC-26 | BI | Air side | -
AC-26.OAD | Outdoor-air damper | AC-26 | AO | Air side | %
AC-26.FRZ | Freeze protection stat | AC-26 | BI | Air side | -
DDC-HSL-11 | FCU-L-N, FCU-L-NE, FCU-L-SE
FCU-L-N.EN | Group enable / schedule | FCU-L-N | BO | Air side | -
FCU-L-N.MODE | Cooling/Heating changeover status | FCU-L-N | BI | Air side | -
FCU-L-N.CWV | Chilled-water group valve | FCU-L-N | AO | Air side | %
FCU-L-N.HWV | Hot-water group valve | FCU-L-N | AO | Air side | %
FCU-L-N.CWBV-F | Chilled-water BV batch fault | FCU-L-N | BI | Air side | -
FCU-L-N.HWBV-F | Hot-water BV batch fault | FCU-L-N | BI | Air side | -
FCU-L-N.RT | Zone reference/return temp | FCU-L-N | AI | Air side | °C
FCU-L-NE.EN | Group enable / schedule | FCU-L-NE | BO | Air side | -
FCU-L-NE.MODE | Cooling/Heating changeover status | FCU-L-NE | BI | Air side | -
FCU-L-NE.CWV | Chilled-water group valve | FCU-L-NE | AO | Air side | %
FCU-L-NE.HWV | Hot-water group valve | FCU-L-NE | AO | Air side | %
FCU-L-NE.CWBV-F | Chilled-water BV batch fault | FCU-L-NE | BI | Air side | -
FCU-L-NE.HWBV-F | Hot-water BV batch fault | FCU-L-NE | BI | Air side | -
FCU-L-NE.RT | Zone reference/return temp | FCU-L-NE | AI | Air side | °C
FCU-L-SE.EN | Group enable / schedule | FCU-L-SE | BO | Air side | -
FCU-L-SE.MODE | Cooling/Heating changeover status | FCU-L-SE | BI | Air side | -
FCU-L-SE.CWV | Chilled-water group valve | FCU-L-SE | AO | Air side | %
FCU-L-SE.HWV | Hot-water group valve | FCU-L-SE | AO | Air side | %
FCU-L-SE.CWBV-F | Chilled-water BV batch fault | FCU-L-SE | BI | Air side | -
FCU-L-SE.HWBV-F | Hot-water BV batch fault | FCU-L-SE | BI | Air side | -
FCU-L-SE.RT | Zone reference/return temp | FCU-L-SE | AI | Air side | °C
DDC-HSL-12 | FCU-L-S, FCU-L-SW
FCU-L-S.EN | Group enable / schedule | FCU-L-S | BO | Air side | -
FCU-L-S.MODE | Cooling/Heating changeover status | FCU-L-S | BI | Air side | -
FCU-L-S.CWV | Chilled-water group valve | FCU-L-S | AO | Air side | %
FCU-L-S.HWV | Hot-water group valve | FCU-L-S | AO | Air side | %
FCU-L-S.CWBV-F | Chilled-water BV batch fault | FCU-L-S | BI | Air side | -
FCU-L-S.HWBV-F | Hot-water BV batch fault | FCU-L-S | BI | Air side | -
FCU-L-S.RT | Zone reference/return temp | FCU-L-S | AI | Air side | °C
FCU-L-SW.EN | Group enable / schedule | FCU-L-SW | BO | Air side | -
FCU-L-SW.MODE | Cooling/Heating changeover status | FCU-L-SW | BI | Air side | -
FCU-L-SW.CWV | Chilled-water group valve | FCU-L-SW | AO | Air side | %
FCU-L-SW.HWV | Hot-water group valve | FCU-L-SW | AO | Air side | %
FCU-L-SW.CWBV-F | Chilled-water BV batch fault | FCU-L-SW | BI | Air side | -
FCU-L-SW.HWBV-F | Hot-water BV batch fault | FCU-L-SW | BI | Air side | -
FCU-L-SW.RT | Zone reference/return temp | FCU-L-SW | AI | Air side | °C
DDC-HSL-13 | SF-6, EF-28, EF-32
SF-6.SS | Start/Stop command | SF-6 | BO | Ventilation | -
SF-6.RUN | Run status | SF-6 | BI | Ventilation | -
SF-6.TRIP | Fault | SF-6 | BI | Ventilation | -
EF-28.SS | Start/Stop command | EF-28 | BO | Ventilation | -
EF-28.RUN | Run status | EF-28 | BI | Ventilation | -
EF-28.TRIP | Fault | EF-28 | BI | Ventilation | -
EF-32.SS | Start/Stop command | EF-32 | BO | Ventilation | -
EF-32.RUN | Run status | EF-32 | BI | Ventilation | -
EF-32.TRIP | Fault | EF-32 | BI | Ventilation | -
DDC-HSL-14 | EF-33, EF-97, RF-7
EF-33.SS | Start/Stop command | EF-33 | BO | Ventilation | -
EF-33.RUN | Run status | EF-33 | BI | Ventilation | -
EF-33.TRIP | Fault | EF-33 | BI | Ventilation | -
EF-97.SS | Start/Stop command | EF-97 | BO | Ventilation | -
EF-97.RUN | Run status | EF-97 | BI | Ventilation | -
EF-97.TRIP | Fault | EF-97 | BI | Ventilation | -
RF-7.SS | Start/Stop command | RF-7 | BO | Ventilation | -
RF-7.RUN | Run status | RF-7 | BI | Ventilation | -
RF-7.TRIP | Fault | RF-7 | BI | Ventilation | -
DDC-HSL-15 | RF-8, RF-9
RF-8.SS | Start/Stop command | RF-8 | BO | Ventilation | -
RF-8.RUN | Run status | RF-8 | BI | Ventilation | -
RF-8.TRIP | Fault | RF-8 | BI | Ventilation | -
RF-9.SS | Start/Stop command | RF-9 | BO | Ventilation | -
RF-9.RUN | Run status | RF-9 | BI | Ventilation | -
RF-9.TRIP | Fault | RF-9 | BI | Ventilation | -
DDC-HSL-16 | POOL-FP
POOL-FP.SS | Start/Stop command | POOL-FP | BO | Common | -
POOL-FP.RUN | Run status | POOL-FP | BI | Common | -
POOL-FP.TRIP | Fault | POOL-FP | BI | Common | -
DDC-HSL-17 | MTR-AHU-KWH
MTR-AHU-KWH | AHU/OAU fans sub-meter | MTR-AHU-KWH | AI | Metering | kWh
LCP-HSH | High-rise distribution panel (高層系統)
DDC-HSH-01 | EX-3-1, EX-3-2
EX-3-1.P-IN | Primary inlet temp (kitchen) | EX-3-1 | AI | Heat source | °C
EX-3-1.S-OUT | Secondary outlet (supply) temp | EX-3-1 | AI | Heat source | °C
EX-3-1.PV | Primary control valve | EX-3-1 | AO | Heat source | %
EX-3-1.PVFB | Primary valve position fb | EX-3-1 | AI | Heat source | %
EX-3-2.P-IN | Primary inlet temp (kitchen) | EX-3-2 | AI | Heat source | °C
EX-3-2.S-OUT | Secondary outlet (supply) temp | EX-3-2 | AI | Heat source | °C
EX-3-2.PV | Primary control valve | EX-3-2 | AO | Heat source | %
EX-3-2.PVFB | Primary valve position fb | EX-3-2 | AI | Heat source | %
DDC-HSH-02 | CP-2-1, CP-2-2, CP-2-3
CP-2-1.RUN | Run status | CP-2-1 | BI | Heat source | -
CP-2-1.TRIP | VFD/pump fault | CP-2-1 | BI | Heat source | -
CP-2-1.SS | Start/Stop command | CP-2-1 | BO | Heat source | -
CP-2-1.SPD | VFD speed command | CP-2-1 | AO | Heat source | %
CP-2-1.SPDFB | VFD speed feedback | CP-2-1 | AI | Heat source | %
CP-2-1.KW | Power | CP-2-1 | AI | Heat source | kW
CP-2-1.FLW | Flow/DP proof | CP-2-1 | BI | Heat source | -
CP-2-2.RUN | Run status | CP-2-2 | BI | Heat source | -
CP-2-2.TRIP | VFD/pump fault | CP-2-2 | BI | Heat source | -
CP-2-2.SS | Start/Stop command | CP-2-2 | BO | Heat source | -
CP-2-2.SPD | VFD speed command | CP-2-2 | AO | Heat source | %
CP-2-2.SPDFB | VFD speed feedback | CP-2-2 | AI | Heat source | %
CP-2-2.KW | Power | CP-2-2 | AI | Heat source | kW
CP-2-2.FLW | Flow/DP proof | CP-2-2 | BI | Heat source | -
CP-2-3.RUN | Run status | CP-2-3 | BI | Heat source | -
CP-2-3.TRIP | VFD/pump fault | CP-2-3 | BI | Heat source | -
CP-2-3.SS | Start/Stop command | CP-2-3 | BO | Heat source | -
CP-2-3.SPD | VFD speed command | CP-2-3 | AO | Heat source | %
CP-2-3.SPDFB | VFD speed feedback | CP-2-3 | AI | Heat source | %
CP-2-3.KW | Power | CP-2-3 | AI | Heat source | kW
CP-2-3.FLW | Flow/DP proof | CP-2-3 | BI | Heat source | -
DDC-HSH-03 | CP-3-1, CP-3-2, CP-6-1
CP-3-1.RUN | Run status | CP-3-1 | BI | Heat source | -
CP-3-1.TRIP | VFD/pump fault | CP-3-1 | BI | Heat source | -
CP-3-1.SS | Start/Stop command | CP-3-1 | BO | Heat source | -
CP-3-1.SPD | VFD speed command | CP-3-1 | AO | Heat source | %
CP-3-1.SPDFB | VFD speed feedback | CP-3-1 | AI | Heat source | %
CP-3-1.KW | Power | CP-3-1 | AI | Heat source | kW
CP-3-1.FLW | Flow/DP proof | CP-3-1 | BI | Heat source | -
CP-3-2.RUN | Run status | CP-3-2 | BI | Heat source | -
CP-3-2.TRIP | VFD/pump fault | CP-3-2 | BI | Heat source | -
CP-3-2.SS | Start/Stop command | CP-3-2 | BO | Heat source | -
CP-3-2.SPD | VFD speed command | CP-3-2 | AO | Heat source | %
CP-3-2.SPDFB | VFD speed feedback | CP-3-2 | AI | Heat source | %
CP-3-2.KW | Power | CP-3-2 | AI | Heat source | kW
CP-3-2.FLW | Flow/DP proof | CP-3-2 | BI | Heat source | -
CP-6-1.RUN | Run status | CP-6-1 | BI | Heat source | -
CP-6-1.TRIP | VFD/pump fault | CP-6-1 | BI | Heat source | -
CP-6-1.SS | Start/Stop command | CP-6-1 | BO | Heat source | -
CP-6-1.SPD | VFD speed command | CP-6-1 | AO | Heat source | %
CP-6-1.SPDFB | VFD speed feedback | CP-6-1 | AI | Heat source | %
CP-6-1.KW | Power | CP-6-1 | AI | Heat source | kW
CP-6-1.FLW | Flow/DP proof | CP-6-1 | BI | Heat source | -
DDC-HSH-04 | CP-6-2
CP-6-2.RUN | Run status | CP-6-2 | BI | Heat source | -
CP-6-2.TRIP | VFD/pump fault | CP-6-2 | BI | Heat source | -
CP-6-2.SS | Start/Stop command | CP-6-2 | BO | Heat source | -
CP-6-2.SPD | VFD speed command | CP-6-2 | AO | Heat source | %
CP-6-2.SPDFB | VFD speed feedback | CP-6-2 | AI | Heat source | %
CP-6-2.KW | Power | CP-6-2 | AI | Heat source | kW
CP-6-2.FLW | Flow/DP proof | CP-6-2 | BI | Heat source | -
DDC-HSH-05 | HP-2-1, HP-2-2, HP-2-3
HP-2-1.RUN | Run status | HP-2-1 | BI | Heat source | -
HP-2-1.TRIP | VFD/pump fault | HP-2-1 | BI | Heat source | -
HP-2-1.SS | Start/Stop command | HP-2-1 | BO | Heat source | -
HP-2-1.SPD | VFD speed command | HP-2-1 | AO | Heat source | %
HP-2-1.SPDFB | VFD speed feedback | HP-2-1 | AI | Heat source | %
HP-2-1.KW | Power | HP-2-1 | AI | Heat source | kW
HP-2-1.FLW | Flow/DP proof | HP-2-1 | BI | Heat source | -
HP-2-2.RUN | Run status | HP-2-2 | BI | Heat source | -
HP-2-2.TRIP | VFD/pump fault | HP-2-2 | BI | Heat source | -
HP-2-2.SS | Start/Stop command | HP-2-2 | BO | Heat source | -
HP-2-2.SPD | VFD speed command | HP-2-2 | AO | Heat source | %
HP-2-2.SPDFB | VFD speed feedback | HP-2-2 | AI | Heat source | %
HP-2-2.KW | Power | HP-2-2 | AI | Heat source | kW
HP-2-2.FLW | Flow/DP proof | HP-2-2 | BI | Heat source | -
HP-2-3.RUN | Run status | HP-2-3 | BI | Heat source | -
HP-2-3.TRIP | VFD/pump fault | HP-2-3 | BI | Heat source | -
HP-2-3.SS | Start/Stop command | HP-2-3 | BO | Heat source | -
HP-2-3.SPD | VFD speed command | HP-2-3 | AO | Heat source | %
HP-2-3.SPDFB | VFD speed feedback | HP-2-3 | AI | Heat source | %
HP-2-3.KW | Power | HP-2-3 | AI | Heat source | kW
HP-2-3.FLW | Flow/DP proof | HP-2-3 | BI | Heat source | -
DDC-HSH-06 | EXT-2
EXT-2.LVL | Tank level | EXT-2 | AI | Heat source | %
EXT-2.HI | High-level alarm | EXT-2 | BI | Heat source | -
EXT-2.LO | Low-level alarm | EXT-2 | BI | Heat source | -
DDC-HSH-07 | ST-2
ST-2.T | Outdoor dry-bulb temp | ST-2 | AI | Common | °C
ST-2.RH | Outdoor humidity | ST-2 | AI | Common | %RH
ST-2.WB | Wet-bulb temp (計測/演算) | ST-2 | AI | Common | °C
DDC-HSH-08 | EVU-11, EVU-12, EVU-13
EVU-11.RUN | Supply fan run status | EVU-11 | BI | Air side | -
EVU-11.TRIP | Supply fan fault | EVU-11 | BI | Air side | -
EVU-11.SS | Supply fan start/stop | EVU-11 | BO | Air side | -
EVU-11.SPD | Supply fan VFD (INV) speed | EVU-11 | AO | Air side | %
EVU-11.SPDFB | Supply fan speed feedback | EVU-11 | AI | Air side | %
EVU-11.SAT | Supply (off-coil) air temp | EVU-11 | AI | Air side | °C
EVU-11.OAT | Outdoor-air temp (unit inlet) | EVU-11 | AI | Air side | °C
EVU-11.OARH | Outdoor-air humidity | EVU-11 | AI | Air side | %RH
EVU-11.CCV | Cooling coil (CHW) valve | EVU-11 | AO | Air side | %
EVU-11.HCV | Heating coil (steam) valve | EVU-11 | AO | Air side | %
EVU-11.HUM | Steam humidifier valve | EVU-11 | AO | Air side | %
EVU-11.FLT | Filter dirty (DP) | EVU-11 | BI | Air side | -
EVU-11.FRZ | Freeze protection stat | EVU-11 | BI | Air side | -
EVU-12.RUN | Supply fan run status | EVU-12 | BI | Air side | -
EVU-12.TRIP | Supply fan fault | EVU-12 | BI | Air side | -
EVU-12.SS | Supply fan start/stop | EVU-12 | BO | Air side | -
EVU-12.SPD | Supply fan VFD (INV) speed | EVU-12 | AO | Air side | %
EVU-12.SPDFB | Supply fan speed feedback | EVU-12 | AI | Air side | %
EVU-12.SAT | Supply (off-coil) air temp | EVU-12 | AI | Air side | °C
EVU-12.OAT | Outdoor-air temp (unit inlet) | EVU-12 | AI | Air side | °C
EVU-12.OARH | Outdoor-air humidity | EVU-12 | AI | Air side | %RH
EVU-12.CCV | Cooling coil (CHW) valve | EVU-12 | AO | Air side | %
EVU-12.HCV | Heating coil (steam) valve | EVU-12 | AO | Air side | %
EVU-12.HUM | Steam humidifier valve | EVU-12 | AO | Air side | %
EVU-12.FLT | Filter dirty (DP) | EVU-12 | BI | Air side | -
EVU-12.FRZ | Freeze protection stat | EVU-12 | BI | Air side | -
EVU-13.RUN | Supply fan run status | EVU-13 | BI | Air side | -
EVU-13.TRIP | Supply fan fault | EVU-13 | BI | Air side | -
EVU-13.SS | Supply fan start/stop | EVU-13 | BO | Air side | -
EVU-13.SPD | Supply fan VFD (INV) speed | EVU-13 | AO | Air side | %
EVU-13.SPDFB | Supply fan speed feedback | EVU-13 | AI | Air side | %
EVU-13.SAT | Supply (off-coil) air temp | EVU-13 | AI | Air side | °C
EVU-13.OAT | Outdoor-air temp (unit inlet) | EVU-13 | AI | Air side | °C
EVU-13.OARH | Outdoor-air humidity | EVU-13 | AI | Air side | %RH
EVU-13.CCV | Cooling coil (CHW) valve | EVU-13 | AO | Air side | %
EVU-13.HCV | Heating coil (steam) valve | EVU-13 | AO | Air side | %
EVU-13.HUM | Steam humidifier valve | EVU-13 | AO | Air side | %
EVU-13.FLT | Filter dirty (DP) | EVU-13 | BI | Air side | -
EVU-13.FRZ | Freeze protection stat | EVU-13 | BI | Air side | -
DDC-HSH-09 | EVU-14, EVU-15
EVU-14.RUN | Supply fan run status | EVU-14 | BI | Air side | -
EVU-14.TRIP | Supply fan fault | EVU-14 | BI | Air side | -
EVU-14.SS | Supply fan start/stop | EVU-14 | BO | Air side | -
EVU-14.SPD | Supply fan speed (fixed) | EVU-14 | AO | Air side | %
EVU-14.SAT | Supply (off-coil) air temp | EVU-14 | AI | Air side | °C
EVU-14.OAT | Outdoor-air temp (unit inlet) | EVU-14 | AI | Air side | °C
EVU-14.OARH | Outdoor-air humidity | EVU-14 | AI | Air side | %RH
EVU-14.CCV | Cooling coil (CHW) valve | EVU-14 | AO | Air side | %
EVU-14.HCV | Heating coil (steam) valve | EVU-14 | AO | Air side | %
EVU-14.HUM | Steam humidifier valve | EVU-14 | AO | Air side | %
EVU-14.FLT | Filter dirty (DP) | EVU-14 | BI | Air side | -
EVU-14.FRZ | Freeze protection stat | EVU-14 | BI | Air side | -
EVU-15.RUN | Supply fan run status | EVU-15 | BI | Air side | -
EVU-15.TRIP | Supply fan fault | EVU-15 | BI | Air side | -
EVU-15.SS | Supply fan start/stop | EVU-15 | BO | Air side | -
EVU-15.SPD | Supply fan speed (fixed) | EVU-15 | AO | Air side | %
EVU-15.SAT | Supply (off-coil) air temp | EVU-15 | AI | Air side | °C
EVU-15.OAT | Outdoor-air temp (unit inlet) | EVU-15 | AI | Air side | °C
EVU-15.OARH | Outdoor-air humidity | EVU-15 | AI | Air side | %RH
EVU-15.CCV | Cooling coil (CHW) valve | EVU-15 | AO | Air side | %
EVU-15.HCV | Heating coil (steam) valve | EVU-15 | AO | Air side | %
EVU-15.HUM | Steam humidifier valve | EVU-15 | AO | Air side | %
EVU-15.FLT | Filter dirty (DP) | EVU-15 | BI | Air side | -
EVU-15.FRZ | Freeze protection stat | EVU-15 | BI | Air side | -
DDC-HSH-10 | FCU-H-N, FCU-H-NE, FCU-H-SE
FCU-H-N.EN | Group enable / schedule | FCU-H-N | BO | Air side | -
FCU-H-N.MODE | Cooling/Heating changeover status | FCU-H-N | BI | Air side | -
FCU-H-N.CWV | Chilled-water group valve | FCU-H-N | AO | Air side | %
FCU-H-N.HWV | Hot-water group valve | FCU-H-N | AO | Air side | %
FCU-H-N.CWBV-F | Chilled-water BV batch fault | FCU-H-N | BI | Air side | -
FCU-H-N.HWBV-F | Hot-water BV batch fault | FCU-H-N | BI | Air side | -
FCU-H-N.RT | Zone reference/return temp | FCU-H-N | AI | Air side | °C
FCU-H-NE.EN | Group enable / schedule | FCU-H-NE | BO | Air side | -
FCU-H-NE.MODE | Cooling/Heating changeover status | FCU-H-NE | BI | Air side | -
FCU-H-NE.CWV | Chilled-water group valve | FCU-H-NE | AO | Air side | %
FCU-H-NE.HWV | Hot-water group valve | FCU-H-NE | AO | Air side | %
FCU-H-NE.CWBV-F | Chilled-water BV batch fault | FCU-H-NE | BI | Air side | -
FCU-H-NE.HWBV-F | Hot-water BV batch fault | FCU-H-NE | BI | Air side | -
FCU-H-NE.RT | Zone reference/return temp | FCU-H-NE | AI | Air side | °C
FCU-H-SE.EN | Group enable / schedule | FCU-H-SE | BO | Air side | -
FCU-H-SE.MODE | Cooling/Heating changeover status | FCU-H-SE | BI | Air side | -
FCU-H-SE.CWV | Chilled-water group valve | FCU-H-SE | AO | Air side | %
FCU-H-SE.HWV | Hot-water group valve | FCU-H-SE | AO | Air side | %
FCU-H-SE.CWBV-F | Chilled-water BV batch fault | FCU-H-SE | BI | Air side | -
FCU-H-SE.HWBV-F | Hot-water BV batch fault | FCU-H-SE | BI | Air side | -
FCU-H-SE.RT | Zone reference/return temp | FCU-H-SE | AI | Air side | °C
DDC-HSH-11 | FCU-H-S, FCU-H-SW
FCU-H-S.EN | Group enable / schedule | FCU-H-S | BO | Air side | -
FCU-H-S.MODE | Cooling/Heating changeover status | FCU-H-S | BI | Air side | -
FCU-H-S.CWV | Chilled-water group valve | FCU-H-S | AO | Air side | %
FCU-H-S.HWV | Hot-water group valve | FCU-H-S | AO | Air side | %
FCU-H-S.CWBV-F | Chilled-water BV batch fault | FCU-H-S | BI | Air side | -
FCU-H-S.HWBV-F | Hot-water BV batch fault | FCU-H-S | BI | Air side | -
FCU-H-S.RT | Zone reference/return temp | FCU-H-S | AI | Air side | °C
FCU-H-SW.EN | Group enable / schedule | FCU-H-SW | BO | Air side | -
FCU-H-SW.MODE | Cooling/Heating changeover status | FCU-H-SW | BI | Air side | -
FCU-H-SW.CWV | Chilled-water group valve | FCU-H-SW | AO | Air side | %
FCU-H-SW.HWV | Hot-water group valve | FCU-H-SW | AO | Air side | %
FCU-H-SW.CWBV-F | Chilled-water BV batch fault | FCU-H-SW | BI | Air side | -
FCU-H-SW.HWBV-F | Hot-water BV batch fault | FCU-H-SW | BI | Air side | -
FCU-H-SW.RT | Zone reference/return temp | FCU-H-SW | AI | Air side | °C
LCP-3637 | 36/37F local heat-source panel (36,37F系統)
DDC-3637-01 | R-1
R-1.RUN | Run status | R-1 | BI | Heat source | -
R-1.TRIP | Common fault / trip | R-1 | BI | Heat source | -
R-1.LR | Local/Remote status | R-1 | BI | Heat source | -
R-1.SS | Start/Stop command | R-1 | BO | Heat source | -
R-1.DMD | Capacity/demand limit | R-1 | AO | Heat source | %
R-1.CHWST | CHW supply (leaving) temp | R-1 | AI | Heat source | °C
R-1.CHWRT | CHW return (entering) temp | R-1 | AI | Heat source | °C
R-1.CWRT | Condenser water leaving temp | R-1 | AI | Heat source | °C
R-1.KW | Electrical input power | R-1 | AI | Heat source | kW
R-1.FLW | Evaporator flow proof | R-1 | BI | Heat source | -
DDC-3637-02 | HEX-1
HEX-1.P-IN | Primary (DHC) inlet temp | HEX-1 | AI | Heat source | °C
HEX-1.P-OUT | Primary (DHC) outlet temp | HEX-1 | AI | Heat source | °C
HEX-1.S-OUT | Secondary (loop) supply temp | HEX-1 | AI | Heat source | °C
HEX-1.S-FLW | Secondary supply flow | HEX-1 | AI | Heat source | m³/h
HEX-1.GJ | DHC thermal-energy meter | HEX-1 | AI | Heat source | MJ
HEX-1.PV | Primary control valve | HEX-1 | AO | Heat source | %
HEX-1.PVFB | Primary valve position fb | HEX-1 | AI | Heat source | %
DDC-3637-03 | CP-7-1, CP-7-2, CP-8-1
CP-7-1.RUN | Run status | CP-7-1 | BI | Heat source | -
CP-7-1.TRIP | VFD/pump fault | CP-7-1 | BI | Heat source | -
CP-7-1.SS | Start/Stop command | CP-7-1 | BO | Heat source | -
CP-7-1.SPD | VFD speed command | CP-7-1 | AO | Heat source | %
CP-7-1.SPDFB | VFD speed feedback | CP-7-1 | AI | Heat source | %
CP-7-1.KW | Power | CP-7-1 | AI | Heat source | kW
CP-7-1.FLW | Flow/DP proof | CP-7-1 | BI | Heat source | -
CP-7-2.RUN | Run status | CP-7-2 | BI | Heat source | -
CP-7-2.TRIP | VFD/pump fault | CP-7-2 | BI | Heat source | -
CP-7-2.SS | Start/Stop command | CP-7-2 | BO | Heat source | -
CP-7-2.SPD | VFD speed command | CP-7-2 | AO | Heat source | %
CP-7-2.SPDFB | VFD speed feedback | CP-7-2 | AI | Heat source | %
CP-7-2.KW | Power | CP-7-2 | AI | Heat source | kW
CP-7-2.FLW | Flow/DP proof | CP-7-2 | BI | Heat source | -
CP-8-1.RUN | Run status | CP-8-1 | BI | Heat source | -
CP-8-1.TRIP | VFD/pump fault | CP-8-1 | BI | Heat source | -
CP-8-1.SS | Start/Stop command | CP-8-1 | BO | Heat source | -
CP-8-1.SPD | VFD speed command | CP-8-1 | AO | Heat source | %
CP-8-1.SPDFB | VFD speed feedback | CP-8-1 | AI | Heat source | %
CP-8-1.KW | Power | CP-8-1 | AI | Heat source | kW
CP-8-1.FLW | Flow/DP proof | CP-8-1 | BI | Heat source | -
DDC-3637-04 | CP-8-2, CP-8-3
CP-8-2.RUN | Run status | CP-8-2 | BI | Heat source | -
CP-8-2.TRIP | VFD/pump fault | CP-8-2 | BI | Heat source | -
CP-8-2.SS | Start/Stop command | CP-8-2 | BO | Heat source | -
CP-8-2.SPD | VFD speed command | CP-8-2 | AO | Heat source | %
CP-8-2.SPDFB | VFD speed feedback | CP-8-2 | AI | Heat source | %
CP-8-2.KW | Power | CP-8-2 | AI | Heat source | kW
CP-8-2.FLW | Flow/DP proof | CP-8-2 | BI | Heat source | -
CP-8-3.RUN | Run status | CP-8-3 | BI | Heat source | -
CP-8-3.TRIP | VFD/pump fault | CP-8-3 | BI | Heat source | -
CP-8-3.SS | Start/Stop command | CP-8-3 | BO | Heat source | -
CP-8-3.SPD | VFD speed command | CP-8-3 | AO | Heat source | %
CP-8-3.SPDFB | VFD speed feedback | CP-8-3 | AI | Heat source | %
CP-8-3.KW | Power | CP-8-3 | AI | Heat source | kW
CP-8-3.FLW | Flow/DP proof | CP-8-3 | BI | Heat source | -
DDC-3637-05 | HP-4-1, HP-4-2
HP-4-1.RUN | Run status | HP-4-1 | BI | Heat source | -
HP-4-1.TRIP | VFD/pump fault | HP-4-1 | BI | Heat source | -
HP-4-1.SS | Start/Stop command | HP-4-1 | BO | Heat source | -
HP-4-1.SPD | VFD speed command | HP-4-1 | AO | Heat source | %
HP-4-1.SPDFB | VFD speed feedback | HP-4-1 | AI | Heat source | %
HP-4-1.KW | Power | HP-4-1 | AI | Heat source | kW
HP-4-1.FLW | Flow/DP proof | HP-4-1 | BI | Heat source | -
HP-4-2.RUN | Run status | HP-4-2 | BI | Heat source | -
HP-4-2.TRIP | VFD/pump fault | HP-4-2 | BI | Heat source | -
HP-4-2.SS | Start/Stop command | HP-4-2 | BO | Heat source | -
HP-4-2.SPD | VFD speed command | HP-4-2 | AO | Heat source | %
HP-4-2.SPDFB | VFD speed feedback | HP-4-2 | AI | Heat source | %
HP-4-2.KW | Power | HP-4-2 | AI | Heat source | kW
HP-4-2.FLW | Flow/DP proof | HP-4-2 | BI | Heat source | -
DDC-3637-06 | EX4, EXT-3
EX4.P-IN | Primary inlet temp (36/37F loop) | EX4 | AI | Heat source | °C
EX4.S-OUT | Secondary outlet (supply) temp | EX4 | AI | Heat source | °C
EX4.PV | Primary control valve | EX4 | AO | Heat source | %
EX4.PVFB | Primary valve position fb | EX4 | AI | Heat source | %
EXT-3.LVL | Tank level | EXT-3 | AI | Heat source | %
EXT-3.HI | High-level alarm | EXT-3 | BI | Heat source | -
EXT-3.LO | Low-level alarm | EXT-3 | BI | Heat source | -
DDC-3637-07 | CHGV-1, CHGV-2
CHGV-1.CMD | Open/close command | CHGV-1 | BO | Heat source | -
CHGV-1.ST | Position status | CHGV-1 | BI | Heat source | -
CHGV-2.CMD | Open/close command | CHGV-2 | BO | Heat source | -
CHGV-2.ST | Position status | CHGV-2 | BI | Heat source | -
DDC-3637-08 | AC-22, AC-23, AC-24
AC-22.RUN | Supply fan run status | AC-22 | BI | Air side | -
AC-22.TRIP | Supply fan fault | AC-22 | BI | Air side | -
AC-22.SS | Supply fan start/stop | AC-22 | BO | Air side | -
AC-22.SPD | Supply fan VFD (INV) speed | AC-22 | AO | Air side | %
AC-22.SPDFB | Supply fan speed feedback | AC-22 | AI | Air side | %
AC-22.SAT | Supply air temp | AC-22 | AI | Air side | °C
AC-22.RAT | Return air temp | AC-22 | AI | Air side | °C
AC-22.CCV | Cooling coil (CHW) valve | AC-22 | AO | Air side | %
AC-22.HCV | Heating coil (steam) valve | AC-22 | AO | Air side | %
AC-22.FLT | Filter dirty (DP) | AC-22 | BI | Air side | -
AC-22.OAD | Outdoor-air damper | AC-22 | AO | Air side | %
AC-22.FRZ | Freeze protection stat | AC-22 | BI | Air side | -
AC-23.RUN | Supply fan run status | AC-23 | BI | Air side | -
AC-23.TRIP | Supply fan fault | AC-23 | BI | Air side | -
AC-23.SS | Supply fan start/stop | AC-23 | BO | Air side | -
AC-23.SPD | Supply fan VFD (INV) speed | AC-23 | AO | Air side | %
AC-23.SPDFB | Supply fan speed feedback | AC-23 | AI | Air side | %
AC-23.SAT | Supply air temp | AC-23 | AI | Air side | °C
AC-23.RAT | Return air temp | AC-23 | AI | Air side | °C
AC-23.CCV | Cooling coil (CHW) valve | AC-23 | AO | Air side | %
AC-23.HCV | Heating coil (steam) valve | AC-23 | AO | Air side | %
AC-23.FLT | Filter dirty (DP) | AC-23 | BI | Air side | -
AC-23.OAD | Outdoor-air damper | AC-23 | AO | Air side | %
AC-23.FRZ | Freeze protection stat | AC-23 | BI | Air side | -
AC-24.RUN | Supply fan run status | AC-24 | BI | Air side | -
AC-24.TRIP | Supply fan fault | AC-24 | BI | Air side | -
AC-24.SS | Supply fan start/stop | AC-24 | BO | Air side | -
AC-24.SPD | Supply fan VFD (INV) speed | AC-24 | AO | Air side | %
AC-24.SPDFB | Supply fan speed feedback | AC-24 | AI | Air side | %
AC-24.SAT | Supply air temp | AC-24 | AI | Air side | °C
AC-24.RAT | Return air temp | AC-24 | AI | Air side | °C
AC-24.CCV | Cooling coil (CHW) valve | AC-24 | AO | Air side | %
AC-24.HCV | Heating coil (steam) valve | AC-24 | AO | Air side | %
AC-24.HUM | Steam humidifier valve | AC-24 | AO | Air side | %
AC-24.RH | Return/space humidity | AC-24 | AI | Air side | %RH
AC-24.FLT | Filter dirty (DP) | AC-24 | BI | Air side | -
AC-24.OAD | Outdoor-air damper | AC-24 | AO | Air side | %
AC-24.FRZ | Freeze protection stat | AC-24 | BI | Air side | -
DDC-3637-09 | AC-25, AC-27
AC-25.RUN | Supply fan run status | AC-25 | BI | Air side | -
AC-25.TRIP | Supply fan fault | AC-25 | BI | Air side | -
AC-25.SS | Supply fan start/stop | AC-25 | BO | Air side | -
AC-25.SPD | Supply fan VFD (INV) speed | AC-25 | AO | Air side | %
AC-25.SPDFB | Supply fan speed feedback | AC-25 | AI | Air side | %
AC-25.SAT | Supply air temp | AC-25 | AI | Air side | °C
AC-25.RAT | Return air temp | AC-25 | AI | Air side | °C
AC-25.CCV | Cooling coil (CHW) valve | AC-25 | AO | Air side | %
AC-25.HCV | Heating coil (steam) valve | AC-25 | AO | Air side | %
AC-25.FLT | Filter dirty (DP) | AC-25 | BI | Air side | -
AC-25.OAD | Outdoor-air damper | AC-25 | AO | Air side | %
AC-25.FRZ | Freeze protection stat | AC-25 | BI | Air side | -
AC-27.RUN | Supply fan run status | AC-27 | BI | Air side | -
AC-27.TRIP | Supply fan fault | AC-27 | BI | Air side | -
AC-27.SS | Supply fan start/stop | AC-27 | BO | Air side | -
AC-27.SPD | Supply fan VFD (INV) speed | AC-27 | AO | Air side | %
AC-27.SPDFB | Supply fan speed feedback | AC-27 | AI | Air side | %
AC-27.SAT | Supply air temp | AC-27 | AI | Air side | °C
AC-27.RAT | Return air temp | AC-27 | AI | Air side | °C
AC-27.CCV | Cooling coil (CHW) valve | AC-27 | AO | Air side | %
AC-27.HCV | Heating coil (steam) valve | AC-27 | AO | Air side | %
AC-27.HUM | Steam humidifier valve | AC-27 | AO | Air side | %
AC-27.RH | Return/space humidity | AC-27 | AI | Air side | %RH
AC-27.FLT | Filter dirty (DP) | AC-27 | BI | Air side | -
AC-27.OAD | Outdoor-air damper | AC-27 | AO | Air side | %
AC-27.FRZ | Freeze protection stat | AC-27 | BI | Air side | -
DDC-3637-10 | FCU-3637
FCU-3637.EN | Group enable / schedule | FCU-3637 | BO | Air side | -
FCU-3637.MODE | Cooling/Heating changeover status | FCU-3637 | BI | Air side | -
FCU-3637.CWV | Chilled-water group valve | FCU-3637 | AO | Air side | %
FCU-3637.HWV | Hot-water group valve | FCU-3637 | AO | Air side | %
FCU-3637.CWBV-F | Chilled-water BV batch fault | FCU-3637 | BI | Air side | -
FCU-3637.HWBV-F | Hot-water BV batch fault | FCU-3637 | BI | Air side | -
FCU-3637.RT | Zone reference/return temp | FCU-3637 | AI | Air side | °C
DDC-3637-11 | EF-82, EF-83, EF-84
EF-82.SS | Start/Stop command | EF-82 | BO | Ventilation | -
EF-82.RUN | Run status | EF-82 | BI | Ventilation | -
EF-82.TRIP | Fault | EF-82 | BI | Ventilation | -
EF-83.SS | Start/Stop command | EF-83 | BO | Ventilation | -
EF-83.RUN | Run status | EF-83 | BI | Ventilation | -
EF-83.TRIP | Fault | EF-83 | BI | Ventilation | -
EF-83.SPD | VFD (INV) speed command | EF-83 | AO | Ventilation | %
EF-83.SPDFB | VFD speed feedback | EF-83 | AI | Ventilation | %
EF-84.SS | Start/Stop command | EF-84 | BO | Ventilation | -
EF-84.RUN | Run status | EF-84 | BI | Ventilation | -
EF-84.TRIP | Fault | EF-84 | BI | Ventilation | -
DDC-3637-12 | EF-85, EF-86, EF-89
EF-85.SS | Start/Stop command | EF-85 | BO | Ventilation | -
EF-85.RUN | Run status | EF-85 | BI | Ventilation | -
EF-85.TRIP | Fault | EF-85 | BI | Ventilation | -
EF-86.SS | Start/Stop command | EF-86 | BO | Ventilation | -
EF-86.RUN | Run status | EF-86 | BI | Ventilation | -
EF-86.TRIP | Fault | EF-86 | BI | Ventilation | -
EF-89.SS | Start/Stop command | EF-89 | BO | Ventilation | -
EF-89.RUN | Run status | EF-89 | BI | Ventilation | -
EF-89.TRIP | Fault | EF-89 | BI | Ventilation | -
DDC-3637-13 | EF-98
EF-98.SS | Start/Stop command | EF-98 | BO | Ventilation | -
EF-98.RUN | Run status | EF-98 | BI | Ventilation | -
EF-98.TRIP | Fault | EF-98 | BI | Ventilation | -
LCP-1F | 1F–2F air-side panel
DDC-1F-01 | AC-7
AC-7.RUN | Supply fan run status | AC-7 | BI | Air side | -
AC-7.TRIP | Supply fan fault | AC-7 | BI | Air side | -
AC-7.SS | Supply fan start/stop | AC-7 | BO | Air side | -
AC-7.SPD | Supply fan VFD (INV) speed | AC-7 | AO | Air side | %
AC-7.SPDFB | Supply fan speed feedback | AC-7 | AI | Air side | %
AC-7.SAT | Supply air temp | AC-7 | AI | Air side | °C
AC-7.RAT | Return air temp | AC-7 | AI | Air side | °C
AC-7.CCV | Cooling coil (CHW) valve | AC-7 | AO | Air side | %
AC-7.HCV | Heating coil (steam) valve | AC-7 | AO | Air side | %
AC-7.FLT | Filter dirty (DP) | AC-7 | BI | Air side | -
AC-7.OAD | Outdoor-air damper | AC-7 | AO | Air side | %
AC-7.FRZ | Freeze protection stat | AC-7 | BI | Air side | -
DDC-1F-02 | EVU-1, EVU-2, EVU-3
EVU-1.RUN | Supply fan run status | EVU-1 | BI | Air side | -
EVU-1.TRIP | Supply fan fault | EVU-1 | BI | Air side | -
EVU-1.SS | Supply fan start/stop | EVU-1 | BO | Air side | -
EVU-1.SPD | Supply fan speed (fixed) | EVU-1 | AO | Air side | %
EVU-1.SAT | Supply (off-coil) air temp | EVU-1 | AI | Air side | °C
EVU-1.OAT | Outdoor-air temp (unit inlet) | EVU-1 | AI | Air side | °C
EVU-1.OARH | Outdoor-air humidity | EVU-1 | AI | Air side | %RH
EVU-1.CCV | Cooling coil (CHW) valve | EVU-1 | AO | Air side | %
EVU-1.HCV | Heating coil (steam) valve | EVU-1 | AO | Air side | %
EVU-1.HUM | Steam humidifier valve | EVU-1 | AO | Air side | %
EVU-1.FLT | Filter dirty (DP) | EVU-1 | BI | Air side | -
EVU-1.FRZ | Freeze protection stat | EVU-1 | BI | Air side | -
EVU-2.RUN | Supply fan run status | EVU-2 | BI | Air side | -
EVU-2.TRIP | Supply fan fault | EVU-2 | BI | Air side | -
EVU-2.SS | Supply fan start/stop | EVU-2 | BO | Air side | -
EVU-2.SPD | Supply fan speed (fixed) | EVU-2 | AO | Air side | %
EVU-2.SAT | Supply (off-coil) air temp | EVU-2 | AI | Air side | °C
EVU-2.OAT | Outdoor-air temp (unit inlet) | EVU-2 | AI | Air side | °C
EVU-2.OARH | Outdoor-air humidity | EVU-2 | AI | Air side | %RH
EVU-2.CCV | Cooling coil (CHW) valve | EVU-2 | AO | Air side | %
EVU-2.HCV | Heating coil (steam) valve | EVU-2 | AO | Air side | %
EVU-2.HUM | Steam humidifier valve | EVU-2 | AO | Air side | %
EVU-2.FLT | Filter dirty (DP) | EVU-2 | BI | Air side | -
EVU-2.FRZ | Freeze protection stat | EVU-2 | BI | Air side | -
EVU-3.RUN | Supply fan run status | EVU-3 | BI | Air side | -
EVU-3.TRIP | Supply fan fault | EVU-3 | BI | Air side | -
EVU-3.SS | Supply fan start/stop | EVU-3 | BO | Air side | -
EVU-3.SPD | Supply fan speed (fixed) | EVU-3 | AO | Air side | %
EVU-3.SAT | Supply (off-coil) air temp | EVU-3 | AI | Air side | °C
EVU-3.OAT | Outdoor-air temp (unit inlet) | EVU-3 | AI | Air side | °C
EVU-3.OARH | Outdoor-air humidity | EVU-3 | AI | Air side | %RH
EVU-3.CCV | Cooling coil (CHW) valve | EVU-3 | AO | Air side | %
EVU-3.HCV | Heating coil (steam) valve | EVU-3 | AO | Air side | %
EVU-3.HUM | Steam humidifier valve | EVU-3 | AO | Air side | %
EVU-3.FLT | Filter dirty (DP) | EVU-3 | BI | Air side | -
EVU-3.FRZ | Freeze protection stat | EVU-3 | BI | Air side | -
DDC-1F-03 | EF-41, EF-42
EF-41.SS | Start/Stop command | EF-41 | BO | Ventilation | -
EF-41.RUN | Run status | EF-41 | BI | Ventilation | -
EF-41.TRIP | Fault | EF-41 | BI | Ventilation | -
EF-42.SS | Start/Stop command | EF-42 | BO | Ventilation | -
EF-42.RUN | Run status | EF-42 | BI | Ventilation | -
EF-42.TRIP | Fault | EF-42 | BI | Ventilation | -
LCP-2F | 2F air-side panel
DDC-2F-01 | AC-8, AC-9, AC-10
AC-8.RUN | Supply fan run status | AC-8 | BI | Air side | -
AC-8.TRIP | Supply fan fault | AC-8 | BI | Air side | -
AC-8.SS | Supply fan start/stop | AC-8 | BO | Air side | -
AC-8.SPD | Supply fan speed (fixed) | AC-8 | AO | Air side | %
AC-8.SAT | Supply air temp | AC-8 | AI | Air side | °C
AC-8.RAT | Return air temp | AC-8 | AI | Air side | °C
AC-8.CCV | Cooling coil (CHW) valve | AC-8 | AO | Air side | %
AC-8.HCV | Heating coil (steam) valve | AC-8 | AO | Air side | %
AC-8.FLT | Filter dirty (DP) | AC-8 | BI | Air side | -
AC-8.OAD | Outdoor-air damper | AC-8 | AO | Air side | %
AC-8.FRZ | Freeze protection stat | AC-8 | BI | Air side | -
AC-9.RUN | Supply fan run status | AC-9 | BI | Air side | -
AC-9.TRIP | Supply fan fault | AC-9 | BI | Air side | -
AC-9.SS | Supply fan start/stop | AC-9 | BO | Air side | -
AC-9.SPD | Supply fan speed (fixed) | AC-9 | AO | Air side | %
AC-9.SAT | Supply air temp | AC-9 | AI | Air side | °C
AC-9.RAT | Return air temp | AC-9 | AI | Air side | °C
AC-9.CCV | Cooling coil (CHW) valve | AC-9 | AO | Air side | %
AC-9.HCV | Heating coil (steam) valve | AC-9 | AO | Air side | %
AC-9.FLT | Filter dirty (DP) | AC-9 | BI | Air side | -
AC-9.OAD | Outdoor-air damper | AC-9 | AO | Air side | %
AC-9.FRZ | Freeze protection stat | AC-9 | BI | Air side | -
AC-10.RUN | Supply fan run status | AC-10 | BI | Air side | -
AC-10.TRIP | Supply fan fault | AC-10 | BI | Air side | -
AC-10.SS | Supply fan start/stop | AC-10 | BO | Air side | -
AC-10.SPD | Supply fan VFD (INV) speed | AC-10 | AO | Air side | %
AC-10.SPDFB | Supply fan speed feedback | AC-10 | AI | Air side | %
AC-10.SAT | Supply air temp | AC-10 | AI | Air side | °C
AC-10.RAT | Return air temp | AC-10 | AI | Air side | °C
AC-10.CCV | Cooling coil (CHW) valve | AC-10 | AO | Air side | %
AC-10.HCV | Heating coil (steam) valve | AC-10 | AO | Air side | %
AC-10.HUM | Steam humidifier valve | AC-10 | AO | Air side | %
AC-10.RH | Return/space humidity | AC-10 | AI | Air side | %RH
AC-10.FLT | Filter dirty (DP) | AC-10 | BI | Air side | -
AC-10.OAD | Outdoor-air damper | AC-10 | AO | Air side | %
AC-10.FRZ | Freeze protection stat | AC-10 | BI | Air side | -
DDC-2F-02 | AC-11, AC-12, AC-13
AC-11.RUN | Supply fan run status | AC-11 | BI | Air side | -
AC-11.TRIP | Supply fan fault | AC-11 | BI | Air side | -
AC-11.SS | Supply fan start/stop | AC-11 | BO | Air side | -
AC-11.SPD | Supply fan VFD (INV) speed | AC-11 | AO | Air side | %
AC-11.SPDFB | Supply fan speed feedback | AC-11 | AI | Air side | %
AC-11.SAT | Supply air temp | AC-11 | AI | Air side | °C
AC-11.RAT | Return air temp | AC-11 | AI | Air side | °C
AC-11.CCV | Cooling coil (CHW) valve | AC-11 | AO | Air side | %
AC-11.HCV | Heating coil (steam) valve | AC-11 | AO | Air side | %
AC-11.FLT | Filter dirty (DP) | AC-11 | BI | Air side | -
AC-11.OAD | Outdoor-air damper | AC-11 | AO | Air side | %
AC-11.FRZ | Freeze protection stat | AC-11 | BI | Air side | -
AC-12.RUN | Supply fan run status | AC-12 | BI | Air side | -
AC-12.TRIP | Supply fan fault | AC-12 | BI | Air side | -
AC-12.SS | Supply fan start/stop | AC-12 | BO | Air side | -
AC-12.SPD | Supply fan VFD (INV) speed | AC-12 | AO | Air side | %
AC-12.SPDFB | Supply fan speed feedback | AC-12 | AI | Air side | %
AC-12.SAT | Supply air temp | AC-12 | AI | Air side | °C
AC-12.RAT | Return air temp | AC-12 | AI | Air side | °C
AC-12.CCV | Cooling coil (CHW) valve | AC-12 | AO | Air side | %
AC-12.HCV | Heating coil (steam) valve | AC-12 | AO | Air side | %
AC-12.FLT | Filter dirty (DP) | AC-12 | BI | Air side | -
AC-12.OAD | Outdoor-air damper | AC-12 | AO | Air side | %
AC-12.FRZ | Freeze protection stat | AC-12 | BI | Air side | -
AC-13.RUN | Supply fan run status | AC-13 | BI | Air side | -
AC-13.TRIP | Supply fan fault | AC-13 | BI | Air side | -
AC-13.SS | Supply fan start/stop | AC-13 | BO | Air side | -
AC-13.SPD | Supply fan VFD (INV) speed | AC-13 | AO | Air side | %
AC-13.SPDFB | Supply fan speed feedback | AC-13 | AI | Air side | %
AC-13.SAT | Supply air temp | AC-13 | AI | Air side | °C
AC-13.RAT | Return air temp | AC-13 | AI | Air side | °C
AC-13.CCV | Cooling coil (CHW) valve | AC-13 | AO | Air side | %
AC-13.HCV | Heating coil (steam) valve | AC-13 | AO | Air side | %
AC-13.FLT | Filter dirty (DP) | AC-13 | BI | Air side | -
AC-13.OAD | Outdoor-air damper | AC-13 | AO | Air side | %
AC-13.FRZ | Freeze protection stat | AC-13 | BI | Air side | -
DDC-2F-03 | EVU-4, EVU-5, EVU-6
EVU-4.RUN | Supply fan run status | EVU-4 | BI | Air side | -
EVU-4.TRIP | Supply fan fault | EVU-4 | BI | Air side | -
EVU-4.SS | Supply fan start/stop | EVU-4 | BO | Air side | -
EVU-4.SPD | Supply fan speed (fixed) | EVU-4 | AO | Air side | %
EVU-4.SAT | Supply (off-coil) air temp | EVU-4 | AI | Air side | °C
EVU-4.OAT | Outdoor-air temp (unit inlet) | EVU-4 | AI | Air side | °C
EVU-4.OARH | Outdoor-air humidity | EVU-4 | AI | Air side | %RH
EVU-4.CCV | Cooling coil (CHW) valve | EVU-4 | AO | Air side | %
EVU-4.HCV | Heating coil (steam) valve | EVU-4 | AO | Air side | %
EVU-4.HUM | Steam humidifier valve | EVU-4 | AO | Air side | %
EVU-4.FLT | Filter dirty (DP) | EVU-4 | BI | Air side | -
EVU-4.FRZ | Freeze protection stat | EVU-4 | BI | Air side | -
EVU-5.RUN | Supply fan run status | EVU-5 | BI | Air side | -
EVU-5.TRIP | Supply fan fault | EVU-5 | BI | Air side | -
EVU-5.SS | Supply fan start/stop | EVU-5 | BO | Air side | -
EVU-5.SPD | Supply fan speed (fixed) | EVU-5 | AO | Air side | %
EVU-5.SAT | Supply (off-coil) air temp | EVU-5 | AI | Air side | °C
EVU-5.OAT | Outdoor-air temp (unit inlet) | EVU-5 | AI | Air side | °C
EVU-5.OARH | Outdoor-air humidity | EVU-5 | AI | Air side | %RH
EVU-5.CCV | Cooling coil (CHW) valve | EVU-5 | AO | Air side | %
EVU-5.HCV | Heating coil (steam) valve | EVU-5 | AO | Air side | %
EVU-5.HUM | Steam humidifier valve | EVU-5 | AO | Air side | %
EVU-5.FLT | Filter dirty (DP) | EVU-5 | BI | Air side | -
EVU-5.FRZ | Freeze protection stat | EVU-5 | BI | Air side | -
EVU-6.RUN | Supply fan run status | EVU-6 | BI | Air side | -
EVU-6.TRIP | Supply fan fault | EVU-6 | BI | Air side | -
EVU-6.SS | Supply fan start/stop | EVU-6 | BO | Air side | -
EVU-6.SPD | Supply fan speed (fixed) | EVU-6 | AO | Air side | %
EVU-6.SAT | Supply (off-coil) air temp | EVU-6 | AI | Air side | °C
EVU-6.OAT | Outdoor-air temp (unit inlet) | EVU-6 | AI | Air side | °C
EVU-6.OARH | Outdoor-air humidity | EVU-6 | AI | Air side | %RH
EVU-6.CCV | Cooling coil (CHW) valve | EVU-6 | AO | Air side | %
EVU-6.HCV | Heating coil (steam) valve | EVU-6 | AO | Air side | %
EVU-6.HUM | Steam humidifier valve | EVU-6 | AO | Air side | %
EVU-6.FLT | Filter dirty (DP) | EVU-6 | BI | Air side | -
EVU-6.FRZ | Freeze protection stat | EVU-6 | BI | Air side | -
DDC-2F-04 | EF-2-1, EF-46, EF-47
EF-2-1.SS | Start/Stop command | EF-2-1 | BO | Ventilation | -
EF-2-1.RUN | Run status | EF-2-1 | BI | Ventilation | -
EF-2-1.TRIP | Fault | EF-2-1 | BI | Ventilation | -
EF-46.SS | Start/Stop command | EF-46 | BO | Ventilation | -
EF-46.RUN | Run status | EF-46 | BI | Ventilation | -
EF-46.TRIP | Fault | EF-46 | BI | Ventilation | -
EF-47.SS | Start/Stop command | EF-47 | BO | Ventilation | -
EF-47.RUN | Run status | EF-47 | BI | Ventilation | -
EF-47.TRIP | Fault | EF-47 | BI | Ventilation | -
LCP-3F | 3F air-side panel
DDC-3F-01 | AC-14, AC-15, AC-16
AC-14.RUN | Supply fan run status | AC-14 | BI | Air side | -
AC-14.TRIP | Supply fan fault | AC-14 | BI | Air side | -
AC-14.SS | Supply fan start/stop | AC-14 | BO | Air side | -
AC-14.SPD | Supply fan VFD (INV) speed | AC-14 | AO | Air side | %
AC-14.SPDFB | Supply fan speed feedback | AC-14 | AI | Air side | %
AC-14.SAT | Supply air temp | AC-14 | AI | Air side | °C
AC-14.RAT | Return air temp | AC-14 | AI | Air side | °C
AC-14.CCV | Cooling coil (CHW) valve | AC-14 | AO | Air side | %
AC-14.HCV | Heating coil (steam) valve | AC-14 | AO | Air side | %
AC-14.HUM | Steam humidifier valve | AC-14 | AO | Air side | %
AC-14.RH | Return/space humidity | AC-14 | AI | Air side | %RH
AC-14.FLT | Filter dirty (DP) | AC-14 | BI | Air side | -
AC-14.OAD | Outdoor-air damper | AC-14 | AO | Air side | %
AC-14.FRZ | Freeze protection stat | AC-14 | BI | Air side | -
AC-15.RUN | Supply fan run status | AC-15 | BI | Air side | -
AC-15.TRIP | Supply fan fault | AC-15 | BI | Air side | -
AC-15.SS | Supply fan start/stop | AC-15 | BO | Air side | -
AC-15.SPD | Supply fan VFD (INV) speed | AC-15 | AO | Air side | %
AC-15.SPDFB | Supply fan speed feedback | AC-15 | AI | Air side | %
AC-15.SAT | Supply air temp | AC-15 | AI | Air side | °C
AC-15.RAT | Return air temp | AC-15 | AI | Air side | °C
AC-15.CCV | Cooling coil (CHW) valve | AC-15 | AO | Air side | %
AC-15.HCV | Heating coil (steam) valve | AC-15 | AO | Air side | %
AC-15.FLT | Filter dirty (DP) | AC-15 | BI | Air side | -
AC-15.OAD | Outdoor-air damper | AC-15 | AO | Air side | %
AC-15.FRZ | Freeze protection stat | AC-15 | BI | Air side | -
AC-16.RUN | Supply fan run status | AC-16 | BI | Air side | -
AC-16.TRIP | Supply fan fault | AC-16 | BI | Air side | -
AC-16.SS | Supply fan start/stop | AC-16 | BO | Air side | -
AC-16.SPD | Supply fan VFD (INV) speed | AC-16 | AO | Air side | %
AC-16.SPDFB | Supply fan speed feedback | AC-16 | AI | Air side | %
AC-16.SAT | Supply air temp | AC-16 | AI | Air side | °C
AC-16.RAT | Return air temp | AC-16 | AI | Air side | °C
AC-16.CCV | Cooling coil (CHW) valve | AC-16 | AO | Air side | %
AC-16.HCV | Heating coil (steam) valve | AC-16 | AO | Air side | %
AC-16.FLT | Filter dirty (DP) | AC-16 | BI | Air side | -
AC-16.OAD | Outdoor-air damper | AC-16 | AO | Air side | %
AC-16.FRZ | Freeze protection stat | AC-16 | BI | Air side | -
DDC-3F-02 | EVU-7
EVU-7.RUN | Supply fan run status | EVU-7 | BI | Air side | -
EVU-7.TRIP | Supply fan fault | EVU-7 | BI | Air side | -
EVU-7.SS | Supply fan start/stop | EVU-7 | BO | Air side | -
EVU-7.SPD | Supply fan speed (fixed) | EVU-7 | AO | Air side | %
EVU-7.SAT | Supply (off-coil) air temp | EVU-7 | AI | Air side | °C
EVU-7.OAT | Outdoor-air temp (unit inlet) | EVU-7 | AI | Air side | °C
EVU-7.OARH | Outdoor-air humidity | EVU-7 | AI | Air side | %RH
EVU-7.CCV | Cooling coil (CHW) valve | EVU-7 | AO | Air side | %
EVU-7.HCV | Heating coil (steam) valve | EVU-7 | AO | Air side | %
EVU-7.HUM | Steam humidifier valve | EVU-7 | AO | Air side | %
EVU-7.FLT | Filter dirty (DP) | EVU-7 | BI | Air side | -
EVU-7.FRZ | Freeze protection stat | EVU-7 | BI | Air side | -
DDC-3F-03 | EF-56, EF-60, EF-61
EF-56.SS | Start/Stop command | EF-56 | BO | Ventilation | -
EF-56.RUN | Run status | EF-56 | BI | Ventilation | -
EF-56.TRIP | Fault | EF-56 | BI | Ventilation | -
EF-60.SS | Start/Stop command | EF-60 | BO | Ventilation | -
EF-60.RUN | Run status | EF-60 | BI | Ventilation | -
EF-60.TRIP | Fault | EF-60 | BI | Ventilation | -
EF-61.SS | Start/Stop command | EF-61 | BO | Ventilation | -
EF-61.RUN | Run status | EF-61 | BI | Ventilation | -
EF-61.TRIP | Fault | EF-61 | BI | Ventilation | -
DDC-3F-04 | EF-62, EF-76, EF-77
EF-62.SS | Start/Stop command | EF-62 | BO | Ventilation | -
EF-62.RUN | Run status | EF-62 | BI | Ventilation | -
EF-62.TRIP | Fault | EF-62 | BI | Ventilation | -
EF-76.SS | Start/Stop command | EF-76 | BO | Ventilation | -
EF-76.RUN | Run status | EF-76 | BI | Ventilation | -
EF-76.TRIP | Fault | EF-76 | BI | Ventilation | -
EF-77.SS | Start/Stop command | EF-77 | BO | Ventilation | -
EF-77.RUN | Run status | EF-77 | BI | Ventilation | -
EF-77.TRIP | Fault | EF-77 | BI | Ventilation | -
LCP-4F | 4F–5F air-side panel
DDC-4F-01 | AC-17, AC-18, AC-19
AC-17.RUN | Supply fan run status | AC-17 | BI | Air side | -
AC-17.TRIP | Supply fan fault | AC-17 | BI | Air side | -
AC-17.SS | Supply fan start/stop | AC-17 | BO | Air side | -
AC-17.SPD | Supply fan VFD (INV) speed | AC-17 | AO | Air side | %
AC-17.SPDFB | Supply fan speed feedback | AC-17 | AI | Air side | %
AC-17.SAT | Supply air temp | AC-17 | AI | Air side | °C
AC-17.RAT | Return air temp | AC-17 | AI | Air side | °C
AC-17.CCV | Cooling coil (CHW) valve | AC-17 | AO | Air side | %
AC-17.HCV | Heating coil (steam) valve | AC-17 | AO | Air side | %
AC-17.FLT | Filter dirty (DP) | AC-17 | BI | Air side | -
AC-17.OAD | Outdoor-air damper | AC-17 | AO | Air side | %
AC-17.FRZ | Freeze protection stat | AC-17 | BI | Air side | -
AC-18.RUN | Supply fan run status | AC-18 | BI | Air side | -
AC-18.TRIP | Supply fan fault | AC-18 | BI | Air side | -
AC-18.SS | Supply fan start/stop | AC-18 | BO | Air side | -
AC-18.SPD | Supply fan VFD (INV) speed | AC-18 | AO | Air side | %
AC-18.SPDFB | Supply fan speed feedback | AC-18 | AI | Air side | %
AC-18.SAT | Supply air temp | AC-18 | AI | Air side | °C
AC-18.RAT | Return air temp | AC-18 | AI | Air side | °C
AC-18.CCV | Cooling coil (CHW) valve | AC-18 | AO | Air side | %
AC-18.HCV | Heating coil (steam) valve | AC-18 | AO | Air side | %
AC-18.FLT | Filter dirty (DP) | AC-18 | BI | Air side | -
AC-18.OAD | Outdoor-air damper | AC-18 | AO | Air side | %
AC-18.FRZ | Freeze protection stat | AC-18 | BI | Air side | -
AC-19.RUN | Supply fan run status | AC-19 | BI | Air side | -
AC-19.TRIP | Supply fan fault | AC-19 | BI | Air side | -
AC-19.SS | Supply fan start/stop | AC-19 | BO | Air side | -
AC-19.SPD | Supply fan VFD (INV) speed | AC-19 | AO | Air side | %
AC-19.SPDFB | Supply fan speed feedback | AC-19 | AI | Air side | %
AC-19.SAT | Supply air temp | AC-19 | AI | Air side | °C
AC-19.RAT | Return air temp | AC-19 | AI | Air side | °C
AC-19.CCV | Cooling coil (CHW) valve | AC-19 | AO | Air side | %
AC-19.HCV | Heating coil (steam) valve | AC-19 | AO | Air side | %
AC-19.HUM | Steam humidifier valve | AC-19 | AO | Air side | %
AC-19.RH | Return/space humidity | AC-19 | AI | Air side | %RH
AC-19.FLT | Filter dirty (DP) | AC-19 | BI | Air side | -
AC-19.OAD | Outdoor-air damper | AC-19 | AO | Air side | %
AC-19.FRZ | Freeze protection stat | AC-19 | BI | Air side | -
DDC-4F-02 | AC-20, AC-21
AC-20.RUN | Supply fan run status | AC-20 | BI | Air side | -
AC-20.TRIP | Supply fan fault | AC-20 | BI | Air side | -
AC-20.SS | Supply fan start/stop | AC-20 | BO | Air side | -
AC-20.SPD | Supply fan VFD (INV) speed | AC-20 | AO | Air side | %
AC-20.SPDFB | Supply fan speed feedback | AC-20 | AI | Air side | %
AC-20.SAT | Supply air temp | AC-20 | AI | Air side | °C
AC-20.RAT | Return air temp | AC-20 | AI | Air side | °C
AC-20.CCV | Cooling coil (CHW) valve | AC-20 | AO | Air side | %
AC-20.HCV | Heating coil (steam) valve | AC-20 | AO | Air side | %
AC-20.FLT | Filter dirty (DP) | AC-20 | BI | Air side | -
AC-20.OAD | Outdoor-air damper | AC-20 | AO | Air side | %
AC-20.FRZ | Freeze protection stat | AC-20 | BI | Air side | -
AC-21.RUN | Supply fan run status | AC-21 | BI | Air side | -
AC-21.TRIP | Supply fan fault | AC-21 | BI | Air side | -
AC-21.SS | Supply fan start/stop | AC-21 | BO | Air side | -
AC-21.SPD | Supply fan VFD (INV) speed | AC-21 | AO | Air side | %
AC-21.SPDFB | Supply fan speed feedback | AC-21 | AI | Air side | %
AC-21.SAT | Supply air temp | AC-21 | AI | Air side | °C
AC-21.RAT | Return air temp | AC-21 | AI | Air side | °C
AC-21.CCV | Cooling coil (CHW) valve | AC-21 | AO | Air side | %
AC-21.HCV | Heating coil (steam) valve | AC-21 | AO | Air side | %
AC-21.FLT | Filter dirty (DP) | AC-21 | BI | Air side | -
AC-21.OAD | Outdoor-air damper | AC-21 | AO | Air side | %
AC-21.FRZ | Freeze protection stat | AC-21 | BI | Air side | -
DDC-4F-03 | EVU-8, EVU-9, EVU-10
EVU-8.RUN | Supply fan run status | EVU-8 | BI | Air side | -
EVU-8.TRIP | Supply fan fault | EVU-8 | BI | Air side | -
EVU-8.SS | Supply fan start/stop | EVU-8 | BO | Air side | -
EVU-8.SPD | Supply fan VFD (INV) speed | EVU-8 | AO | Air side | %
EVU-8.SPDFB | Supply fan speed feedback | EVU-8 | AI | Air side | %
EVU-8.SAT | Supply (off-coil) air temp | EVU-8 | AI | Air side | °C
EVU-8.OAT | Outdoor-air temp (unit inlet) | EVU-8 | AI | Air side | °C
EVU-8.OARH | Outdoor-air humidity | EVU-8 | AI | Air side | %RH
EVU-8.CCV | Cooling coil (CHW) valve | EVU-8 | AO | Air side | %
EVU-8.HCV | Heating coil (steam) valve | EVU-8 | AO | Air side | %
EVU-8.HUM | Steam humidifier valve | EVU-8 | AO | Air side | %
EVU-8.FLT | Filter dirty (DP) | EVU-8 | BI | Air side | -
EVU-8.FRZ | Freeze protection stat | EVU-8 | BI | Air side | -
EVU-9.RUN | Supply fan run status | EVU-9 | BI | Air side | -
EVU-9.TRIP | Supply fan fault | EVU-9 | BI | Air side | -
EVU-9.SS | Supply fan start/stop | EVU-9 | BO | Air side | -
EVU-9.SPD | Supply fan VFD (INV) speed | EVU-9 | AO | Air side | %
EVU-9.SPDFB | Supply fan speed feedback | EVU-9 | AI | Air side | %
EVU-9.SAT | Supply (off-coil) air temp | EVU-9 | AI | Air side | °C
EVU-9.OAT | Outdoor-air temp (unit inlet) | EVU-9 | AI | Air side | °C
EVU-9.OARH | Outdoor-air humidity | EVU-9 | AI | Air side | %RH
EVU-9.CCV | Cooling coil (CHW) valve | EVU-9 | AO | Air side | %
EVU-9.HCV | Heating coil (steam) valve | EVU-9 | AO | Air side | %
EVU-9.HUM | Steam humidifier valve | EVU-9 | AO | Air side | %
EVU-9.FLT | Filter dirty (DP) | EVU-9 | BI | Air side | -
EVU-9.FRZ | Freeze protection stat | EVU-9 | BI | Air side | -
EVU-10.RUN | Supply fan run status | EVU-10 | BI | Air side | -
EVU-10.TRIP | Supply fan fault | EVU-10 | BI | Air side | -
EVU-10.SS | Supply fan start/stop | EVU-10 | BO | Air side | -
EVU-10.SPD | Supply fan VFD (INV) speed | EVU-10 | AO | Air side | %
EVU-10.SPDFB | Supply fan speed feedback | EVU-10 | AI | Air side | %
EVU-10.SAT | Supply (off-coil) air temp | EVU-10 | AI | Air side | °C
EVU-10.OAT | Outdoor-air temp (unit inlet) | EVU-10 | AI | Air side | °C
EVU-10.OARH | Outdoor-air humidity | EVU-10 | AI | Air side | %RH
EVU-10.CCV | Cooling coil (CHW) valve | EVU-10 | AO | Air side | %
EVU-10.HCV | Heating coil (steam) valve | EVU-10 | AO | Air side | %
EVU-10.HUM | Steam humidifier valve | EVU-10 | AO | Air side | %
EVU-10.FLT | Filter dirty (DP) | EVU-10 | BI | Air side | -
EVU-10.FRZ | Freeze protection stat | EVU-10 | BI | Air side | -
DDC-4F-04 | EF-54, EF-55, EF-57
EF-54.SS | Start/Stop command | EF-54 | BO | Ventilation | -
EF-54.RUN | Run status | EF-54 | BI | Ventilation | -
EF-54.TRIP | Fault | EF-54 | BI | Ventilation | -
EF-55.SS | Start/Stop command | EF-55 | BO | Ventilation | -
EF-55.RUN | Run status | EF-55 | BI | Ventilation | -
EF-55.TRIP | Fault | EF-55 | BI | Ventilation | -
EF-57.SS | Start/Stop command | EF-57 | BO | Ventilation | -
EF-57.RUN | Run status | EF-57 | BI | Ventilation | -
EF-57.TRIP | Fault | EF-57 | BI | Ventilation | -
DDC-4F-05 | EF-58, EF-59, EF-59-2
EF-58.SS | Start/Stop command | EF-58 | BO | Ventilation | -
EF-58.RUN | Run status | EF-58 | BI | Ventilation | -
EF-58.TRIP | Fault | EF-58 | BI | Ventilation | -
EF-59.SS | Start/Stop command | EF-59 | BO | Ventilation | -
EF-59.RUN | Run status | EF-59 | BI | Ventilation | -
EF-59.TRIP | Fault | EF-59 | BI | Ventilation | -
EF-59-2.SS | Start/Stop command | EF-59-2 | BO | Ventilation | -
EF-59-2.RUN | Run status | EF-59-2 | BI | Ventilation | -
EF-59-2.TRIP | Fault | EF-59-2 | BI | Ventilation | -
DDC-4F-06 | EF-67, EF-69, EF-70
EF-67.SS | Start/Stop command | EF-67 | BO | Ventilation | -
EF-67.RUN | Run status | EF-67 | BI | Ventilation | -
EF-67.TRIP | Fault | EF-67 | BI | Ventilation | -
EF-69.SS | Start/Stop command | EF-69 | BO | Ventilation | -
EF-69.RUN | Run status | EF-69 | BI | Ventilation | -
EF-69.TRIP | Fault | EF-69 | BI | Ventilation | -
EF-70.SS | Start/Stop command | EF-70 | BO | Ventilation | -
EF-70.RUN | Run status | EF-70 | BI | Ventilation | -
EF-70.TRIP | Fault | EF-70 | BI | Ventilation | -
EF-70.SPD | VFD (INV) speed command | EF-70 | AO | Ventilation | %
EF-70.SPDFB | VFD speed feedback | EF-70 | AI | Ventilation | %
DDC-4F-07 | EF-71
EF-71.SS | Start/Stop command | EF-71 | BO | Ventilation | -
EF-71.RUN | Run status | EF-71 | BI | Ventilation | -
EF-71.TRIP | Fault | EF-71 | BI | Ventilation | -
LCP-PKG | Packaged-unit & refrigeration panel
DDC-PKG-01 | PAC-1-1, PAC-1-2, PAC-2
PAC-1-1.RUN | Run status | PAC-1-1 | BI | Packaged units | -
PAC-1-1.TRIP | Fault / alarm | PAC-1-1 | BI | Packaged units | -
PAC-1-1.SS | Start/Stop command | PAC-1-1 | BO | Packaged units | -
PAC-1-2.RUN | Run status | PAC-1-2 | BI | Packaged units | -
PAC-1-2.TRIP | Fault / alarm | PAC-1-2 | BI | Packaged units | -
PAC-1-2.SS | Start/Stop command | PAC-1-2 | BO | Packaged units | -
PAC-2.RUN | Run status | PAC-2 | BI | Packaged units | -
PAC-2.TRIP | Fault / alarm | PAC-2 | BI | Packaged units | -
PAC-2.SS | Start/Stop command | PAC-2 | BO | Packaged units | -
DDC-PKG-02 | PAC-3, PAC-4, PAC-5
PAC-3.RUN | Run status | PAC-3 | BI | Packaged units | -
PAC-3.TRIP | Fault / alarm | PAC-3 | BI | Packaged units | -
PAC-3.SS | Start/Stop command | PAC-3 | BO | Packaged units | -
PAC-4.RUN | Run status | PAC-4 | BI | Packaged units | -
PAC-4.TRIP | Fault / alarm | PAC-4 | BI | Packaged units | -
PAC-4.SS | Start/Stop command | PAC-4 | BO | Packaged units | -
PAC-5.RUN | Run status | PAC-5 | BI | Packaged units | -
PAC-5.TRIP | Fault / alarm | PAC-5 | BI | Packaged units | -
PAC-5.SS | Start/Stop command | PAC-5 | BO | Packaged units | -
DDC-PKG-03 | PCU-1-1, PCU-1-2, PCU-5
PCU-1-1.RUN | Run status | PCU-1-1 | BI | Packaged units | -
PCU-1-1.TRIP | Fault / alarm | PCU-1-1 | BI | Packaged units | -
PCU-1-1.SS | Start/Stop command | PCU-1-1 | BO | Packaged units | -
PCU-1-2.RUN | Run status | PCU-1-2 | BI | Packaged units | -
PCU-1-2.TRIP | Fault / alarm | PCU-1-2 | BI | Packaged units | -
PCU-1-2.SS | Start/Stop command | PCU-1-2 | BO | Packaged units | -
PCU-5.RUN | Run status | PCU-5 | BI | Packaged units | -
PCU-5.TRIP | Fault / alarm | PCU-5 | BI | Packaged units | -
PCU-5.SS | Start/Stop command | PCU-5 | BO | Packaged units | -
DDC-PKG-04 | PCU-6, PCU-7, PCU-8
PCU-6.RUN | Run status | PCU-6 | BI | Packaged units | -
PCU-6.TRIP | Fault / alarm | PCU-6 | BI | Packaged units | -
PCU-6.SS | Start/Stop command | PCU-6 | BO | Packaged units | -
PCU-7.RUN | Run status | PCU-7 | BI | Packaged units | -
PCU-7.TRIP | Fault / alarm | PCU-7 | BI | Packaged units | -
PCU-7.SS | Start/Stop command | PCU-7 | BO | Packaged units | -
PCU-8.RUN | Run status | PCU-8 | BI | Packaged units | -
PCU-8.TRIP | Fault / alarm | PCU-8 | BI | Packaged units | -
PCU-8.SS | Start/Stop command | PCU-8 | BO | Packaged units | -
DDC-PKG-05 | PCU-10, PCU-11, PCU-12
PCU-10.RUN | Run status | PCU-10 | BI | Packaged units | -
PCU-10.TRIP | Fault / alarm | PCU-10 | BI | Packaged units | -
PCU-10.SS | Start/Stop command | PCU-10 | BO | Packaged units | -
PCU-11.RUN | Run status | PCU-11 | BI | Packaged units | -
PCU-11.TRIP | Fault / alarm | PCU-11 | BI | Packaged units | -
PCU-11.SS | Start/Stop command | PCU-11 | BO | Packaged units | -
PCU-12.RUN | Run status | PCU-12 | BI | Packaged units | -
PCU-12.TRIP | Fault / alarm | PCU-12 | BI | Packaged units | -
PCU-12.SS | Start/Stop command | PCU-12 | BO | Packaged units | -
DDC-PKG-06 | PCU-13, PMAC-1
PCU-13.RUN | Run status | PCU-13 | BI | Packaged units | -
PCU-13.TRIP | Fault / alarm | PCU-13 | BI | Packaged units | -
PCU-13.SS | Start/Stop command | PCU-13 | BO | Packaged units | -
PMAC-1.RUN | Run status | PMAC-1 | BI | Packaged units | -
PMAC-1.TRIP | Fault / alarm | PMAC-1 | BI | Packaged units | -
PMAC-1.SS | Start/Stop command | PMAC-1 | BO | Packaged units | -
DDC-PKG-07 | REFR-1
REFR-1.ALM1 | Cold-store/refrigeration alarm — B1F 主厨房一括 | REFR-1 | BI | Packaged units | -
REFR-1.ALM2 | Cold-store/refrigeration alarm — B1F 厨房冷蔵庫異常一括 | REFR-1 | BI | Packaged units | -
REFR-1.ALM3 | Cold-store/refrigeration alarm — MR-1 ル・パティオ厨房 | REFR-1 | BI | Packaged units | -
REFR-1.ALM4 | Cold-store/refrigeration alarm — 2F ゴミ処理室 | REFR-1 | BI | Packaged units | -
REFR-1.ALM5 | Cold-store/refrigeration alarm — 2F カスケイド厨房 | REFR-1 | BI | Packaged units | -
REFR-1.ALM6 | Cold-store/refrigeration alarm — 調理冷蔵庫 | REFR-1 | BI | Packaged units | -
REFR-1.ALM7 | Cold-store/refrigeration alarm — 雲海厨房 | REFR-1 | BI | Packaged units | -
LCP-LTG | Common-area & facade lighting panel
DDC-LTG-01 | LTG-AVIATION, LTG-NEON, LTG-BALCONY-L
LTG-AVIATION.CMD | On/Off command | LTG-AVIATION | BO | Lighting | -
LTG-AVIATION.ST | Group status | LTG-AVIATION | BI | Lighting | -
LTG-NEON.CMD | On/Off command | LTG-NEON | BO | Lighting | -
LTG-NEON.ST | Group status | LTG-NEON | BI | Lighting | -
LTG-BALCONY-L.CMD | On/Off command | LTG-BALCONY-L | BO | Lighting | -
LTG-BALCONY-L.ST | Group status | LTG-BALCONY-L | BI | Lighting | -
DDC-LTG-02 | LTG-BALCONY-H, LTG-CORRIDOR, LTG-LOBBY
LTG-BALCONY-H.CMD | On/Off command | LTG-BALCONY-H | BO | Lighting | -
LTG-BALCONY-H.ST | Group status | LTG-BALCONY-H | BI | Lighting | -
LTG-CORRIDOR.CMD | On/Off command | LTG-CORRIDOR | BO | Lighting | -
LTG-CORRIDOR.ST | Group status | LTG-CORRIDOR | BI | Lighting | -
LTG-LOBBY.CMD | On/Off command | LTG-LOBBY | BO | Lighting | -
LTG-LOBBY.ST | Group status | LTG-LOBBY | BI | Lighting | -
DDC-LTG-03 | LTG-SOFFIT, LTG-TENANT
LTG-SOFFIT.CMD | On/Off command | LTG-SOFFIT | BO | Lighting | -
LTG-SOFFIT.ST | Group status | LTG-SOFFIT | BI | Lighting | -
LTG-TENANT.CMD | On/Off command | LTG-TENANT | BO | Lighting | -
LTG-TENANT.ST | Group status | LTG-TENANT | BI | Lighting | -

## Flat
Panel | Panel description | Controller | Device ID | Point Tag | I/O | System | Units | Description | Notes / Basis
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.CS-T | AI | DHC interface | °C | Supply (CS) temp | DHC冷水受入 ~7°C
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.CR-T | AI | DHC interface | °C | Return (CR) temp | DHC冷水返送
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.CS-P | AI | DHC interface | MPa | Supply header pressure
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.CR-P | AI | DHC interface | MPa | Return header pressure
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.FLW | AI | DHC interface | m³/h | Intake flow
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.GJ | AI | DHC interface | GJ | Thermal-energy meter | GJ/h + integrated; thermal-demand control
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.CV | AO | DHC interface | % | Intake control valve | Modulate to building load
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.CVFB | AI | DHC interface | % | Intake valve position fb
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.ISOL | BO | DHC interface | - | Intake isolation valve open/close
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-01 | DHC-CHW | DHC-CHW.ISOL-ST | BI | DHC interface | - | Isolation valve status
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.SS-P | AI | DHC interface | MPa | Supply (SS 8k) pressure | ~0.8 MPa
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.MASS | AI | DHC interface | t/h | Steam mass-flow meter | t/h + integrated kg
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.PRV | AO | DHC interface | % | PRV 8k->2k reducing valve | 0.8->0.2 MPa
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.SSH2-P | AI | DHC interface | MPa | Reduced (SSH 2k) pressure | ~0.2 MPa
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.ISOL | BO | DHC interface | - | Main isolation valve open/close | Season enable + OA lockout
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.ISOL-ST | BI | DHC interface | - | Isolation valve status
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-02 | DHC-STEAM | DHC-STEAM.HR-M | AI | DHC interface | L | Condensate (HR) return meter | Hot-return to DHC via HWT-1
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-03 | HWT-1 | HWT-1.LVL | AI | Heat source | % | Tank level
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-03 | HWT-1 | HWT-1.HI | BI | Heat source | - | High-level alarm
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-03 | HWT-1 | HWT-1.LO | BI | Heat source | - | Low-level alarm
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-03 | HWT-1 | HWT-1.T | AI | Heat source | °C | Condensate temp
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-03 | HWT-1 | HWT-1.MU | BO | Heat source | - | Make-up water valve
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.RUN | BI | Heat source | - | Run status
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.SS | BO | Heat source | - | Start/Stop command
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.SPD | AO | Heat source | % | VFD speed command | HP-5; HWT-1 -> DHC hot-return
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-1 | HP-5-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.RUN | BI | Heat source | - | Run status
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.SS | BO | Heat source | - | Start/Stop command
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.SPD | AO | Heat source | % | VFD speed command | HP-5; HWT-1 -> DHC hot-return
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-5-2 | HP-5-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.RUN | BI | Heat source | - | Run status
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.SS | BO | Heat source | - | Start/Stop command
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.SPD | AO | Heat source | % | VFD speed command | HP-3; serves B1F 厨房 AC-5/6/7
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-04 | HP-3-1 | HP-3-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.RUN | BI | Heat source | - | Run status
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.SS | BO | Heat source | - | Start/Stop command
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.SPD | AO | Heat source | % | VFD speed command | HP-3; serves B1F 厨房 AC-5/6/7
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.KW | AI | Heat source | kW | Power
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-05 | HP-3-2 | HP-3-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-06 | MTR-ELEC-MAIN | MTR-ELEC-MAIN | AI | Metering | kWh | Main electricity (kWh) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-06 | MTR-GAS-MAIN | MTR-GAS-MAIN | AI | Metering | m³ | City gas (m³) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-06 | MTR-WATER-MAIN | MTR-WATER-MAIN | AI | Metering | m³ | City water (m³) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-07 | MTR-DHC-CHW | MTR-DHC-CHW | AI | Metering | GJ | DHC chilled-water energy (受入) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-07 | MTR-DHC-STEAM | MTR-DHC-STEAM | AI | Metering | t/h | DHC steam energy (受入) | Integrating meter; thermal-demand & peak limiting
LCP-DHC | DHC intake & hot-well panel | DDC-DHC-07 | MTR-DHC-COND | MTR-DHC-COND | AI | Metering | L | DHC condensate return (HR) | Integrating meter; thermal-demand & peak limiting
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-1 | CT-1-1.RUN | BI | Condenser water | - | Fan run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-1 | CT-1-1.TRIP | BI | Condenser water | - | Fan INV fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-1 | CT-1-1.SS | BO | Condenser water | - | Fan start/stop
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-1 | CT-1-1.SPD | AO | Condenser water | % | Fan VFD speed command | Wet-bulb + approach reset
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-1 | CT-1-1.SPDFB | AI | Condenser water | % | Fan speed feedback
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-2 | CT-1-2.RUN | BI | Condenser water | - | Fan run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-2 | CT-1-2.TRIP | BI | Condenser water | - | Fan INV fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-2 | CT-1-2.SS | BO | Condenser water | - | Fan start/stop
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-2 | CT-1-2.SPD | AO | Condenser water | % | Fan VFD speed command | Wet-bulb + approach reset
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1-2 | CT-1-2.SPDFB | AI | Condenser water | % | Fan speed feedback
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1 | CT-1.LVL | AI | Condenser water | % | Basin water level
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1 | CT-1.MU | BO | Condenser water | - | Make-up water valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1 | CT-1.BLD | BO | Condenser water | - | Bleed/blowdown valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1 | CT-1.DRY | BI | Condenser water | - | Low-water (渇水) alarm
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1 | CT-1.CHEM | BI | Condenser water | - | Chemical dosing (薬注) batch fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-01 | CT-1 | CT-1.EH | BO | Condenser water | - | Basin heater (E/H) enable | Freeze protection
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-1 | CT-2-1.RUN | BI | Condenser water | - | Fan run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-1 | CT-2-1.TRIP | BI | Condenser water | - | Fan INV fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-1 | CT-2-1.SS | BO | Condenser water | - | Fan start/stop
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-1 | CT-2-1.SPD | AO | Condenser water | % | Fan VFD speed command | Wet-bulb + approach reset
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-1 | CT-2-1.SPDFB | AI | Condenser water | % | Fan speed feedback
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-2 | CT-2-2.RUN | BI | Condenser water | - | Fan run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-2 | CT-2-2.TRIP | BI | Condenser water | - | Fan INV fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-2 | CT-2-2.SS | BO | Condenser water | - | Fan start/stop
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-2 | CT-2-2.SPD | AO | Condenser water | % | Fan VFD speed command | Wet-bulb + approach reset
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2-2 | CT-2-2.SPDFB | AI | Condenser water | % | Fan speed feedback
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.LVL | AI | Condenser water | % | Basin water level
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.MU | BO | Condenser water | - | Make-up water valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.BLD | BO | Condenser water | - | Bleed/blowdown valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.DRY | BI | Condenser water | - | Low-water (渇水) alarm
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.CHEM | BI | Condenser water | - | Chemical dosing (薬注) batch fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.EH | BO | Condenser water | - | Basin heater (E/H) enable | Freeze protection
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.FILT-RUN | BI | Condenser water | - | Filtration (ろ過) pump run
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-02 | CT-2 | CT-2.FILT-SS | BO | Condenser water | - | Filtration pump start/stop
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3-1 | CT-3-1.RUN | BI | Condenser water | - | Fan run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3-1 | CT-3-1.TRIP | BI | Condenser water | - | Fan INV fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3-1 | CT-3-1.SS | BO | Condenser water | - | Fan start/stop
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3-1 | CT-3-1.SPD | AO | Condenser water | % | Fan VFD speed command | Wet-bulb + approach reset
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3-1 | CT-3-1.SPDFB | AI | Condenser water | % | Fan speed feedback
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3 | CT-3.LVL | AI | Condenser water | % | Basin water level
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3 | CT-3.MU | BO | Condenser water | - | Make-up water valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3 | CT-3.BLD | BO | Condenser water | - | Bleed/blowdown valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3 | CT-3.DRY | BI | Condenser water | - | Low-water (渇水) alarm
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3 | CT-3.CHEM | BI | Condenser water | - | Chemical dosing (薬注) batch fault
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-03 | CT-3 | CT-3.EH | BO | Condenser water | - | Basin heater (E/H) enable | Freeze protection
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-1 | CDP-1-1.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-1 | CDP-1-1.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-1 | CDP-1-1.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-1 | CDP-1-1.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-2 | CDP-1-2.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-2 | CDP-1-2.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-2 | CDP-1-2.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-2 | CDP-1-2.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-3 | CDP-1-3.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-3 | CDP-1-3.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-3 | CDP-1-3.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-04 | CDP-1-3 | CDP-1-3.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-1 | CDP-2-1.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-1 | CDP-2-1.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-1 | CDP-2-1.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-1 | CDP-2-1.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-2 | CDP-2-2.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-2 | CDP-2-2.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-2 | CDP-2-2.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-2-2 | CDP-2-2.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-3-1 | CDP-3-1.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-3-1 | CDP-3-1.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-3-1 | CDP-3-1.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-05 | CDP-3-1 | CDP-3-1.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-06 | CDP-3-2 | CDP-3-2.RUN | BI | Condenser water | - | Run status
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-06 | CDP-3-2 | CDP-3-2.TRIP | BI | Condenser water | - | Fault / breaker trip
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-06 | CDP-3-2 | CDP-3-2.SS | BO | Condenser water | - | Start/Stop command | Group start (群起動); interlock w/ CT + load
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-06 | CDP-3-2 | CDP-3-2.FLW | BI | Condenser water | - | Flow/DP proof
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EX-1 | EX-1.EN | BO | Condenser water | - | Free-cooling enable / changeover | Low wet-bulb winter free-cooling
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EX-1 | EX-1.ST | AI | Condenser water | °C | CHW-side leaving temp
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EX-1 | EX-1.CV | AO | Condenser water | % | CW-side control valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EMHX-1 | EMHX-1.EN | BO | Condenser water | - | Emergency cooling enable | 低層階非常用; from DHC冷水受入ヘッダ
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EMHX-1 | EMHX-1.ST | AI | Condenser water | °C | Cooling-water leaving temp
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EMHX-1 | EMHX-1.ISOL | BO | Condenser water | - | DHC-side isolation valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EMHX-2 | EMHX-2.EN | BO | Condenser water | - | Emergency cooling enable | 低層階非常用; from DHC冷水受入ヘッダ
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EMHX-2 | EMHX-2.ST | AI | Condenser water | °C | Cooling-water leaving temp
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-07 | EMHX-2 | EMHX-2.ISOL | BO | Condenser water | - | DHC-side isolation valve
LCP-CT | Cooling-tower & condenser-water panel | DDC-CT-08 | MTR-CDW-KWH | MTR-CDW-KWH | AI | Metering | kWh | Cooling-tower/condenser sub-meter | Integrating meter; thermal-demand & peak limiting
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-1 | EX-2-1.P-IN | AI | Heat source | °C | Primary inlet temp (laundry)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-1 | EX-2-1.S-OUT | AI | Heat source | °C | Secondary outlet (supply) temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-1 | EX-2-1.PV | AO | Heat source | % | Primary control valve | Modulate to hold S-OUT
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-1 | EX-2-1.PVFB | AI | Heat source | % | Primary valve position fb
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-2 | EX-2-2.P-IN | AI | Heat source | °C | Primary inlet temp (laundry)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-2 | EX-2-2.S-OUT | AI | Heat source | °C | Secondary outlet (supply) temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-2 | EX-2-2.PV | AO | Heat source | % | Primary control valve | Modulate to hold S-OUT
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-01 | EX-2-2 | EX-2-2.PVFB | AI | Heat source | % | Primary valve position fb
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.SPD | AO | Heat source | % | VFD speed command | CP-1; sequenced/群起動; VFD; DP-reset
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-1 | CP-1-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.SPD | AO | Heat source | % | VFD speed command | CP-1; sequenced/群起動; VFD; DP-reset
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-2 | CP-1-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.SPD | AO | Heat source | % | VFD speed command | CP-1; sequenced/群起動; VFD; DP-reset
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-02 | CP-1-3 | CP-1-3.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.SPD | AO | Heat source | % | VFD speed command | CP-4; open/close + duty rotation
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-1 | CP-4-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.SPD | AO | Heat source | % | VFD speed command | CP-4; open/close + duty rotation
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-4-2 | CP-4-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.SPD | AO | Heat source | % | VFD speed command | CP-5
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-03 | CP-5-1 | CP-5-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.SPD | AO | Heat source | % | VFD speed command | CP-5
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-04 | CP-5-2 | CP-5-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.SPD | AO | Heat source | % | VFD speed command | HP-1; sequenced; 4-pipe heating loop
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-1 | HP-1-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.SPD | AO | Heat source | % | VFD speed command | HP-1; sequenced; 4-pipe heating loop
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-2 | HP-1-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.RUN | BI | Heat source | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.SS | BO | Heat source | - | Start/Stop command
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.SPD | AO | Heat source | % | VFD speed command | HP-1; sequenced; 4-pipe heating loop
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.KW | AI | Heat source | kW | Power
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-05 | HP-1-3 | HP-1-3.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-06 | EXT-1 | EXT-1.LVL | AI | Heat source | % | Tank level
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-06 | EXT-1 | EXT-1.HI | BI | Heat source | - | High-level alarm
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-06 | EXT-1 | EXT-1.LO | BI | Heat source | - | Low-level alarm
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-07 | ST-1 | ST-1.T | AI | Common | °C | Outdoor dry-bulb temp | 低層 OA sensor
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-07 | ST-1 | ST-1.RH | AI | Common | %RH | Outdoor humidity
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-07 | ST-1 | ST-1.WB | AI | Common | °C | Wet-bulb temp (計測/演算) | Drives CW setpoint + free-cooling
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.SPD | AO | Air side | % | Supply fan speed (fixed) | INFERRED / no INV control per schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-1 | AC-1.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.SPD | AO | Air side | % | Supply fan speed (fixed) | INFERRED / no INV control per schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-2 | AC-2.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.SPD | AO | Air side | % | Supply fan speed (fixed) | INFERRED / no INV control per schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-08 | AC-3 | AC-3.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-4 | AC-4.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-5 | AC-5.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-09 | AC-6 | AC-6.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.RUN | BI | Air side | - | Supply fan run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.TRIP | BI | Air side | - | Supply fan fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.RAT | AI | Air side | °C | Return air temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.OAD | AO | Air side | % | Outdoor-air damper
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-10 | AC-26 | AC-26.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-N | FCU-L-N.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-NE | FCU-L-NE.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-11 | FCU-L-SE | FCU-L-SE.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-S | FCU-L-S.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-12 | FCU-L-SW | FCU-L-SW.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | SF-6 | SF-6.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | SF-6 | SF-6.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | SF-6 | SF-6.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | EF-28 | EF-28.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | EF-28 | EF-28.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | EF-28 | EF-28.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | EF-32 | EF-32.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | EF-32 | EF-32.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-13 | EF-32 | EF-32.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | EF-33 | EF-33.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | EF-33 | EF-33.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | EF-33 | EF-33.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | EF-97 | EF-97.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | EF-97 | EF-97.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | EF-97 | EF-97.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | RF-7 | RF-7.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | RF-7 | RF-7.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-14 | RF-7 | RF-7.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-15 | RF-8 | RF-8.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-15 | RF-8 | RF-8.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-15 | RF-8 | RF-8.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-15 | RF-9 | RF-9.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-15 | RF-9 | RF-9.RUN | BI | Ventilation | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-15 | RF-9 | RF-9.TRIP | BI | Ventilation | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-16 | POOL-FP | POOL-FP.SS | BO | Common | - | Start/Stop command | Time schedule 8:00-19:00
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-16 | POOL-FP | POOL-FP.RUN | BI | Common | - | Run status
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-16 | POOL-FP | POOL-FP.TRIP | BI | Common | - | Fault
LCP-HSL | Low-rise distribution panel (低層系統) | DDC-HSL-17 | MTR-AHU-KWH | MTR-AHU-KWH | AI | Metering | kWh | AHU/OAU fans sub-meter | Integrating meter; thermal-demand & peak limiting
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-1 | EX-3-1.P-IN | AI | Heat source | °C | Primary inlet temp (kitchen)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-1 | EX-3-1.S-OUT | AI | Heat source | °C | Secondary outlet (supply) temp
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-1 | EX-3-1.PV | AO | Heat source | % | Primary control valve | Modulate to hold S-OUT
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-1 | EX-3-1.PVFB | AI | Heat source | % | Primary valve position fb
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-2 | EX-3-2.P-IN | AI | Heat source | °C | Primary inlet temp (kitchen)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-2 | EX-3-2.S-OUT | AI | Heat source | °C | Secondary outlet (supply) temp
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-2 | EX-3-2.PV | AO | Heat source | % | Primary control valve | Modulate to hold S-OUT
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-01 | EX-3-2 | EX-3-2.PVFB | AI | Heat source | % | Primary valve position fb
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.SPD | AO | Heat source | % | VFD speed command | CP-2; sequenced/群起動; VFD; DP-reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-1 | CP-2-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.SPD | AO | Heat source | % | VFD speed command | CP-2; sequenced/群起動; VFD; DP-reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-2 | CP-2-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.SPD | AO | Heat source | % | VFD speed command | CP-2; sequenced/群起動; VFD; DP-reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-02 | CP-2-3 | CP-2-3.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.SPD | AO | Heat source | % | VFD speed command | CP-3; INV; control-flow l/m
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-1 | CP-3-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.SPD | AO | Heat source | % | VFD speed command | CP-3; INV; control-flow l/m
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-3-2 | CP-3-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.SPD | AO | Heat source | % | VFD speed command | CP-6; 順序切替 ON:№1優先
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-03 | CP-6-1 | CP-6-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.SPD | AO | Heat source | % | VFD speed command | CP-6; 順序切替 ON:№1優先
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-04 | CP-6-2 | CP-6-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.SPD | AO | Heat source | % | VFD speed command | HP-2; sequenced; 4-pipe heating loop
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-1 | HP-2-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.SPD | AO | Heat source | % | VFD speed command | HP-2; sequenced; 4-pipe heating loop
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-2 | HP-2-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.RUN | BI | Heat source | - | Run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.TRIP | BI | Heat source | - | VFD/pump fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.SS | BO | Heat source | - | Start/Stop command
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.SPD | AO | Heat source | % | VFD speed command | HP-2; sequenced; 4-pipe heating loop
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.KW | AI | Heat source | kW | Power
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-05 | HP-2-3 | HP-2-3.FLW | BI | Heat source | - | Flow/DP proof
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-06 | EXT-2 | EXT-2.LVL | AI | Heat source | % | Tank level
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-06 | EXT-2 | EXT-2.HI | BI | Heat source | - | High-level alarm
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-06 | EXT-2 | EXT-2.LO | BI | Heat source | - | Low-level alarm
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-07 | ST-2 | ST-2.T | AI | Common | °C | Outdoor dry-bulb temp | 高層 OA sensor
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-07 | ST-2 | ST-2.RH | AI | Common | %RH | Outdoor humidity
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-07 | ST-2 | ST-2.WB | AI | Common | °C | Wet-bulb temp (計測/演算) | Drives CW setpoint + free-cooling
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.RUN | BI | Air side | - | Supply fan run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.TRIP | BI | Air side | - | Supply fan fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.HUM | AO | Air side | % | Steam humidifier valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-11 | EVU-11.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.RUN | BI | Air side | - | Supply fan run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.TRIP | BI | Air side | - | Supply fan fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.HUM | AO | Air side | % | Steam humidifier valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-12 | EVU-12.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.RUN | BI | Air side | - | Supply fan run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.TRIP | BI | Air side | - | Supply fan fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.HUM | AO | Air side | % | Steam humidifier valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-08 | EVU-13 | EVU-13.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.RUN | BI | Air side | - | Supply fan run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.TRIP | BI | Air side | - | Supply fan fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.HUM | AO | Air side | % | Steam humidifier valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-14 | EVU-14.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.RUN | BI | Air side | - | Supply fan run status
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.TRIP | BI | Air side | - | Supply fan fault
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.HUM | AO | Air side | % | Steam humidifier valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.FLT | BI | Air side | - | Filter dirty (DP)
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-09 | EVU-15 | EVU-15.FRZ | BI | Air side | - | Freeze protection stat
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-N | FCU-H-N.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-NE | FCU-H-NE.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-10 | FCU-H-SE | FCU-H-SE.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-S | FCU-H-S.RT | AI | Air side | °C | Zone reference/return temp
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.EN | BO | Air side | - | Group enable / schedule | DHC 4-pipe; season changeover
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.CWV | AO | Air side | % | Chilled-water group valve
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-HSH | High-rise distribution panel (高層系統) | DDC-HSH-11 | FCU-H-SW | FCU-H-SW.RT | AI | Air side | °C | Zone reference/return temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.TRIP | BI | Heat source | - | Common fault / trip
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.LR | BI | Heat source | - | Local/Remote status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.SS | BO | Heat source | - | Start/Stop command | 36/37F local chiller; BACKUP to DHC (チラーバックアップ); source changeover valves
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.DMD | AO | Heat source | % | Capacity/demand limit | Demand-limit / soft-load
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.CHWST | AI | Heat source | °C | CHW supply (leaving) temp | Design 7°C
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.CHWRT | AI | Heat source | °C | CHW return (entering) temp | Design 12°C
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.CWRT | AI | Heat source | °C | Condenser water leaving temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.KW | AI | Heat source | kW | Electrical input power | Ebara screw RHS DW202M2: 370 kW cool / 82.2 kW in (COP 4.5); 2×45 kW screw comp, R-407C
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-01 | R-1 | R-1.FLW | BI | Heat source | - | Evaporator flow proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.P-IN | AI | Heat source | °C | Primary (DHC) inlet temp | 36/37F DHC tie-in (チラーバックアップ)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.P-OUT | AI | Heat source | °C | Primary (DHC) outlet temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.S-OUT | AI | Heat source | °C | Secondary (loop) supply temp | Loop CHW setpoint
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.S-FLW | AI | Heat source | m³/h | Secondary supply flow
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.GJ | AI | Heat source | MJ | DHC thermal-energy meter | m³/h + MJ on the graphic
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.PV | AO | Heat source | % | Primary control valve | Modulate to hold S-OUT
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-02 | HEX-1 | HEX-1.PVFB | AI | Heat source | % | Primary valve position fb
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.SPD | AO | Heat source | % | VFD speed command | CP-7; duty/standby; 発停/故障
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-1 | CP-7-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.SPD | AO | Heat source | % | VFD speed command | CP-7; duty/standby; 発停/故障
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-7-2 | CP-7-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.SPD | AO | Heat source | % | VFD speed command | CP-8; DHC side of HEX-1; metered
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-03 | CP-8-1 | CP-8-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.SPD | AO | Heat source | % | VFD speed command | CP-8; DHC side of HEX-1; metered
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-2 | CP-8-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.SPD | AO | Heat source | % | VFD speed command | CP-8; DHC side of HEX-1; metered
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-04 | CP-8-3 | CP-8-3.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.SPD | AO | Heat source | % | VFD speed command | HP-4; EX4 secondary -> FCU/AC/EVU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-1 | HP-4-1.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.RUN | BI | Heat source | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.TRIP | BI | Heat source | - | VFD/pump fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.SS | BO | Heat source | - | Start/Stop command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.SPD | AO | Heat source | % | VFD speed command | HP-4; EX4 secondary -> FCU/AC/EVU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.SPDFB | AI | Heat source | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.KW | AI | Heat source | kW | Power
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-05 | HP-4-2 | HP-4-2.FLW | BI | Heat source | - | Flow/DP proof
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EX4 | EX4.P-IN | AI | Heat source | °C | Primary inlet temp (36/37F loop)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EX4 | EX4.S-OUT | AI | Heat source | °C | Secondary outlet (supply) temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EX4 | EX4.PV | AO | Heat source | % | Primary control valve | Modulate to hold S-OUT
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EX4 | EX4.PVFB | AI | Heat source | % | Primary valve position fb
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EXT-3 | EXT-3.LVL | AI | Heat source | % | Tank level
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EXT-3 | EXT-3.HI | BI | Heat source | - | High-level alarm
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-06 | EXT-3 | EXT-3.LO | BI | Heat source | - | Low-level alarm
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-07 | CHGV-1 | CHGV-1.CMD | BO | Heat source | - | Open/close command | R-1 evaporator branch valve (open = chiller mode)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-07 | CHGV-1 | CHGV-1.ST | BI | Heat source | - | Position status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-07 | CHGV-2 | CHGV-2.CMD | BO | Heat source | - | Open/close command | Through-main valve (open = DHC bypass mode)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-07 | CHGV-2 | CHGV-2.ST | BI | Heat source | - | Position status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.RUN | BI | Air side | - | Supply fan run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.TRIP | BI | Air side | - | Supply fan fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.RAT | AI | Air side | °C | Return air temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.OAD | AO | Air side | % | Outdoor-air damper
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-22 | AC-22.FRZ | BI | Air side | - | Freeze protection stat
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.RUN | BI | Air side | - | Supply fan run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.TRIP | BI | Air side | - | Supply fan fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.RAT | AI | Air side | °C | Return air temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.OAD | AO | Air side | % | Outdoor-air damper
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-23 | AC-23.FRZ | BI | Air side | - | Freeze protection stat
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.RUN | BI | Air side | - | Supply fan run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.TRIP | BI | Air side | - | Supply fan fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.RAT | AI | Air side | °C | Return air temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.HUM | AO | Air side | % | Steam humidifier valve
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.RH | AI | Air side | %RH | Return/space humidity
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.OAD | AO | Air side | % | Outdoor-air damper
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-08 | AC-24 | AC-24.FRZ | BI | Air side | - | Freeze protection stat
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.RUN | BI | Air side | - | Supply fan run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.TRIP | BI | Air side | - | Supply fan fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.RAT | AI | Air side | °C | Return air temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.OAD | AO | Air side | % | Outdoor-air damper
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-25 | AC-25.FRZ | BI | Air side | - | Freeze protection stat
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.RUN | BI | Air side | - | Supply fan run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.TRIP | BI | Air side | - | Supply fan fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.RAT | AI | Air side | °C | Return air temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.HUM | AO | Air side | % | Steam humidifier valve
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.RH | AI | Air side | %RH | Return/space humidity
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.OAD | AO | Air side | % | Outdoor-air damper
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-09 | AC-27 | AC-27.FRZ | BI | Air side | - | Freeze protection stat
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.EN | BO | Air side | - | Group enable / schedule | 36/37F: EX4 secondary loop (DHC/R-1 source)
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.MODE | BI | Air side | - | Cooling/Heating changeover status | 順序/季節切替
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.CWV | AO | Air side | % | Chilled-water group valve
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.HWV | AO | Air side | % | Hot-water group valve | Deadband vs cooling
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.CWBV-F | BI | Air side | - | Chilled-water BV batch fault | 冷水BV一括故障
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.HWBV-F | BI | Air side | - | Hot-water BV batch fault | 温水BV一括故障
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-10 | FCU-3637 | FCU-3637.RT | AI | Air side | °C | Zone reference/return temp
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-82 | EF-82.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-82 | EF-82.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-82 | EF-82.TRIP | BI | Ventilation | - | Fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-83 | EF-83.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-83 | EF-83.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-83 | EF-83.TRIP | BI | Ventilation | - | Fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-83 | EF-83.SPD | AO | Ventilation | % | VFD (INV) speed command
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-83 | EF-83.SPDFB | AI | Ventilation | % | VFD speed feedback
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-84 | EF-84.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-84 | EF-84.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-11 | EF-84 | EF-84.TRIP | BI | Ventilation | - | Fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-85 | EF-85.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-85 | EF-85.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-85 | EF-85.TRIP | BI | Ventilation | - | Fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-86 | EF-86.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-86 | EF-86.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-86 | EF-86.TRIP | BI | Ventilation | - | Fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-89 | EF-89.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-89 | EF-89.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-12 | EF-89 | EF-89.TRIP | BI | Ventilation | - | Fault
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-13 | EF-98 | EF-98.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-13 | EF-98 | EF-98.RUN | BI | Ventilation | - | Run status
LCP-3637 | 36/37F local heat-source panel (36,37F系統) | DDC-3637-13 | EF-98 | EF-98.TRIP | BI | Ventilation | - | Fault
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.RUN | BI | Air side | - | Supply fan run status
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.TRIP | BI | Air side | - | Supply fan fault
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.RAT | AI | Air side | °C | Return air temp
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.FLT | BI | Air side | - | Filter dirty (DP)
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.OAD | AO | Air side | % | Outdoor-air damper
LCP-1F | 1F–2F air-side panel | DDC-1F-01 | AC-7 | AC-7.FRZ | BI | Air side | - | Freeze protection stat
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.RUN | BI | Air side | - | Supply fan run status
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.TRIP | BI | Air side | - | Supply fan fault
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.HUM | AO | Air side | % | Steam humidifier valve
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.FLT | BI | Air side | - | Filter dirty (DP)
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-1 | EVU-1.FRZ | BI | Air side | - | Freeze protection stat
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.RUN | BI | Air side | - | Supply fan run status
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.TRIP | BI | Air side | - | Supply fan fault
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.HUM | AO | Air side | % | Steam humidifier valve
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.FLT | BI | Air side | - | Filter dirty (DP)
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-2 | EVU-2.FRZ | BI | Air side | - | Freeze protection stat
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.RUN | BI | Air side | - | Supply fan run status
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.TRIP | BI | Air side | - | Supply fan fault
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.HUM | AO | Air side | % | Steam humidifier valve
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.FLT | BI | Air side | - | Filter dirty (DP)
LCP-1F | 1F–2F air-side panel | DDC-1F-02 | EVU-3 | EVU-3.FRZ | BI | Air side | - | Freeze protection stat
LCP-1F | 1F–2F air-side panel | DDC-1F-03 | EF-41 | EF-41.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-1F | 1F–2F air-side panel | DDC-1F-03 | EF-41 | EF-41.RUN | BI | Ventilation | - | Run status
LCP-1F | 1F–2F air-side panel | DDC-1F-03 | EF-41 | EF-41.TRIP | BI | Ventilation | - | Fault
LCP-1F | 1F–2F air-side panel | DDC-1F-03 | EF-42 | EF-42.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-1F | 1F–2F air-side panel | DDC-1F-03 | EF-42 | EF-42.RUN | BI | Ventilation | - | Run status
LCP-1F | 1F–2F air-side panel | DDC-1F-03 | EF-42 | EF-42.TRIP | BI | Ventilation | - | Fault
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.SPD | AO | Air side | % | Supply fan speed (fixed) | INFERRED / no INV control per schedule
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.RAT | AI | Air side | °C | Return air temp
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.OAD | AO | Air side | % | Outdoor-air damper
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-8 | AC-8.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.SPD | AO | Air side | % | Supply fan speed (fixed) | INFERRED / no INV control per schedule
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.RAT | AI | Air side | °C | Return air temp
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.OAD | AO | Air side | % | Outdoor-air damper
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-9 | AC-9.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.RAT | AI | Air side | °C | Return air temp
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.HUM | AO | Air side | % | Steam humidifier valve
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.RH | AI | Air side | %RH | Return/space humidity
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.OAD | AO | Air side | % | Outdoor-air damper
LCP-2F | 2F air-side panel | DDC-2F-01 | AC-10 | AC-10.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.RAT | AI | Air side | °C | Return air temp
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.OAD | AO | Air side | % | Outdoor-air damper
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-11 | AC-11.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.RAT | AI | Air side | °C | Return air temp
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.OAD | AO | Air side | % | Outdoor-air damper
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-12 | AC-12.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.RAT | AI | Air side | °C | Return air temp
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.OAD | AO | Air side | % | Outdoor-air damper
LCP-2F | 2F air-side panel | DDC-2F-02 | AC-13 | AC-13.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.HUM | AO | Air side | % | Steam humidifier valve
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-4 | EVU-4.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.HUM | AO | Air side | % | Steam humidifier valve
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-5 | EVU-5.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.RUN | BI | Air side | - | Supply fan run status
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.TRIP | BI | Air side | - | Supply fan fault
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.HUM | AO | Air side | % | Steam humidifier valve
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.FLT | BI | Air side | - | Filter dirty (DP)
LCP-2F | 2F air-side panel | DDC-2F-03 | EVU-6 | EVU-6.FRZ | BI | Air side | - | Freeze protection stat
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-2-1 | EF-2-1.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-2-1 | EF-2-1.RUN | BI | Ventilation | - | Run status
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-2-1 | EF-2-1.TRIP | BI | Ventilation | - | Fault
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-46 | EF-46.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-46 | EF-46.RUN | BI | Ventilation | - | Run status
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-46 | EF-46.TRIP | BI | Ventilation | - | Fault
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-47 | EF-47.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-47 | EF-47.RUN | BI | Ventilation | - | Run status
LCP-2F | 2F air-side panel | DDC-2F-04 | EF-47 | EF-47.TRIP | BI | Ventilation | - | Fault
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.RUN | BI | Air side | - | Supply fan run status
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.TRIP | BI | Air side | - | Supply fan fault
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.RAT | AI | Air side | °C | Return air temp
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.HUM | AO | Air side | % | Steam humidifier valve
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.RH | AI | Air side | %RH | Return/space humidity
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.OAD | AO | Air side | % | Outdoor-air damper
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-14 | AC-14.FRZ | BI | Air side | - | Freeze protection stat
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.RUN | BI | Air side | - | Supply fan run status
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.TRIP | BI | Air side | - | Supply fan fault
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.RAT | AI | Air side | °C | Return air temp
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.OAD | AO | Air side | % | Outdoor-air damper
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-15 | AC-15.FRZ | BI | Air side | - | Freeze protection stat
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.RUN | BI | Air side | - | Supply fan run status
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.TRIP | BI | Air side | - | Supply fan fault
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.RAT | AI | Air side | °C | Return air temp
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.OAD | AO | Air side | % | Outdoor-air damper
LCP-3F | 3F air-side panel | DDC-3F-01 | AC-16 | AC-16.FRZ | BI | Air side | - | Freeze protection stat
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.RUN | BI | Air side | - | Supply fan run status
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.TRIP | BI | Air side | - | Supply fan fault
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.SPD | AO | Air side | % | Supply fan speed (fixed) | No INV control per schedule
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.HUM | AO | Air side | % | Steam humidifier valve
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.FLT | BI | Air side | - | Filter dirty (DP)
LCP-3F | 3F air-side panel | DDC-3F-02 | EVU-7 | EVU-7.FRZ | BI | Air side | - | Freeze protection stat
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-56 | EF-56.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-56 | EF-56.RUN | BI | Ventilation | - | Run status
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-56 | EF-56.TRIP | BI | Ventilation | - | Fault
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-60 | EF-60.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-60 | EF-60.RUN | BI | Ventilation | - | Run status
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-60 | EF-60.TRIP | BI | Ventilation | - | Fault
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-61 | EF-61.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-61 | EF-61.RUN | BI | Ventilation | - | Run status
LCP-3F | 3F air-side panel | DDC-3F-03 | EF-61 | EF-61.TRIP | BI | Ventilation | - | Fault
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-62 | EF-62.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-62 | EF-62.RUN | BI | Ventilation | - | Run status
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-62 | EF-62.TRIP | BI | Ventilation | - | Fault
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-76 | EF-76.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-76 | EF-76.RUN | BI | Ventilation | - | Run status
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-76 | EF-76.TRIP | BI | Ventilation | - | Fault
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-77 | EF-77.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-77 | EF-77.RUN | BI | Ventilation | - | Run status
LCP-3F | 3F air-side panel | DDC-3F-04 | EF-77 | EF-77.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.RAT | AI | Air side | °C | Return air temp
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.OAD | AO | Air side | % | Outdoor-air damper
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-17 | AC-17.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.RAT | AI | Air side | °C | Return air temp
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.OAD | AO | Air side | % | Outdoor-air damper
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-18 | AC-18.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.RAT | AI | Air side | °C | Return air temp
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.HUM | AO | Air side | % | Steam humidifier valve
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.RH | AI | Air side | %RH | Return/space humidity
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.OAD | AO | Air side | % | Outdoor-air damper
LCP-4F | 4F–5F air-side panel | DDC-4F-01 | AC-19 | AC-19.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.SAT | AI | Air side | °C | Supply air temp | SAT/RAT setpoint schedule
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.RAT | AI | Air side | °C | Return air temp
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.OAD | AO | Air side | % | Outdoor-air damper
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-20 | AC-20.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.SS | BO | Air side | - | Supply fan start/stop | Time/event schedule; banquet 'occ by event'
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV output schedule 0.4-1.0
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.SAT | AI | Air side | °C | Supply air temp | Kitchen SAT 5-12°C
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.RAT | AI | Air side | °C | Return air temp
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.CCV | AO | Air side | % | Cooling coil (CHW) valve | PID to SAT; zero-energy band
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband vs CCV
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.OAD | AO | Air side | % | Outdoor-air damper
LCP-4F | 4F–5F air-side panel | DDC-4F-02 | AC-21 | AC-21.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.HUM | AO | Air side | % | Steam humidifier valve
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-8 | EVU-8.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.HUM | AO | Air side | % | Steam humidifier valve
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-9 | EVU-9.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.RUN | BI | Air side | - | Supply fan run status
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.TRIP | BI | Air side | - | Supply fan fault
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.SS | BO | Air side | - | Supply fan start/stop | Time schedule; night setback
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.SPD | AO | Air side | % | Supply fan VFD (INV) speed | INV schedule; demand vent
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.SPDFB | AI | Air side | % | Supply fan speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.SAT | AI | Air side | °C | Supply (off-coil) air temp | Seasonal SAT reset
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.OAT | AI | Air side | °C | Outdoor-air temp (unit inlet)
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.OARH | AI | Air side | %RH | Outdoor-air humidity
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.CCV | AO | Air side | % | Cooling coil (CHW) valve
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.HCV | AO | Air side | % | Heating coil (steam) valve | Season enable; deadband
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.HUM | AO | Air side | % | Steam humidifier valve
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.FLT | BI | Air side | - | Filter dirty (DP)
LCP-4F | 4F–5F air-side panel | DDC-4F-03 | EVU-10 | EVU-10.FRZ | BI | Air side | - | Freeze protection stat
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-54 | EF-54.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-54 | EF-54.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-54 | EF-54.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-55 | EF-55.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-55 | EF-55.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-55 | EF-55.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-57 | EF-57.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-57 | EF-57.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-04 | EF-57 | EF-57.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-58 | EF-58.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-58 | EF-58.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-58 | EF-58.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-59 | EF-59.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-59 | EF-59.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-59 | EF-59.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-59-2 | EF-59-2.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-59-2 | EF-59-2.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-05 | EF-59-2 | EF-59-2.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-67 | EF-67.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-67 | EF-67.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-67 | EF-67.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-69 | EF-69.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-69 | EF-69.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-69 | EF-69.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-70 | EF-70.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-70 | EF-70.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-70 | EF-70.TRIP | BI | Ventilation | - | Fault
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-70 | EF-70.SPD | AO | Ventilation | % | VFD (INV) speed command
LCP-4F | 4F–5F air-side panel | DDC-4F-06 | EF-70 | EF-70.SPDFB | AI | Ventilation | % | VFD speed feedback
LCP-4F | 4F–5F air-side panel | DDC-4F-07 | EF-71 | EF-71.SS | BO | Ventilation | - | Start/Stop command | Interlock w/ parent AHU
LCP-4F | 4F–5F air-side panel | DDC-4F-07 | EF-71 | EF-71.RUN | BI | Ventilation | - | Run status
LCP-4F | 4F–5F air-side panel | DDC-4F-07 | EF-71 | EF-71.TRIP | BI | Ventilation | - | Fault
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-1 | PAC-1-1.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-1 | PAC-1-1.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-1 | PAC-1-1.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-2 | PAC-1-2.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-2 | PAC-1-2.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-1-2 | PAC-1-2.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-2 | PAC-2.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-2 | PAC-2.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-01 | PAC-2 | PAC-2.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-3 | PAC-3.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-3 | PAC-3.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-3 | PAC-3.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-4 | PAC-4.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-4 | PAC-4.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-4 | PAC-4.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-5 | PAC-5.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-5 | PAC-5.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-02 | PAC-5 | PAC-5.SS | BO | Packaged units | - | Start/Stop command | 24/7 (electrical room)
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-1-1 | PCU-1-1.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-1-1 | PCU-1-1.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-1-1 | PCU-1-1.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-1-2 | PCU-1-2.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-1-2 | PCU-1-2.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-1-2 | PCU-1-2.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-5 | PCU-5.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-5 | PCU-5.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-03 | PCU-5 | PCU-5.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-6 | PCU-6.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-6 | PCU-6.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-6 | PCU-6.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-7 | PCU-7.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-7 | PCU-7.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-7 | PCU-7.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-8 | PCU-8.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-8 | PCU-8.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-04 | PCU-8 | PCU-8.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-10 | PCU-10.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-10 | PCU-10.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-10 | PCU-10.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-11 | PCU-11.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-11 | PCU-11.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-11 | PCU-11.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-12 | PCU-12.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-12 | PCU-12.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-05 | PCU-12 | PCU-12.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-06 | PCU-13 | PCU-13.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-06 | PCU-13 | PCU-13.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-06 | PCU-13 | PCU-13.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-06 | PMAC-1 | PMAC-1.RUN | BI | Packaged units | - | Run status
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-06 | PMAC-1 | PMAC-1.TRIP | BI | Packaged units | - | Fault / alarm
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-06 | PMAC-1 | PMAC-1.SS | BO | Packaged units | - | Start/Stop command | Time/occupancy schedule
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM1 | BI | Packaged units | - | Cold-store/refrigeration alarm — B1F 主厨房一括 | 冷蔵庫異常; condenser-water rejected
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM2 | BI | Packaged units | - | Cold-store/refrigeration alarm — B1F 厨房冷蔵庫異常一括 | 冷蔵庫異常; condenser-water rejected
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM3 | BI | Packaged units | - | Cold-store/refrigeration alarm — MR-1 ル・パティオ厨房 | 冷蔵庫異常; condenser-water rejected
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM4 | BI | Packaged units | - | Cold-store/refrigeration alarm — 2F ゴミ処理室 | 冷蔵庫異常; condenser-water rejected
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM5 | BI | Packaged units | - | Cold-store/refrigeration alarm — 2F カスケイド厨房 | 冷蔵庫異常; condenser-water rejected
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM6 | BI | Packaged units | - | Cold-store/refrigeration alarm — 調理冷蔵庫 | 冷蔵庫異常; condenser-water rejected
LCP-PKG | Packaged-unit & refrigeration panel | DDC-PKG-07 | REFR-1 | REFR-1.ALM7 | BI | Packaged units | - | Cold-store/refrigeration alarm — 雲海厨房 | 冷蔵庫異常; condenser-water rejected
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-01 | LTG-AVIATION | LTG-AVIATION.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-01 | LTG-AVIATION | LTG-AVIATION.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-01 | LTG-NEON | LTG-NEON.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-01 | LTG-NEON | LTG-NEON.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-01 | LTG-BALCONY-L | LTG-BALCONY-L.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-01 | LTG-BALCONY-L | LTG-BALCONY-L.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-02 | LTG-BALCONY-H | LTG-BALCONY-H.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-02 | LTG-BALCONY-H | LTG-BALCONY-H.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-02 | LTG-CORRIDOR | LTG-CORRIDOR.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-02 | LTG-CORRIDOR | LTG-CORRIDOR.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-02 | LTG-LOBBY | LTG-LOBBY.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-02 | LTG-LOBBY | LTG-LOBBY.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-03 | LTG-SOFFIT | LTG-SOFFIT.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-03 | LTG-SOFFIT | LTG-SOFFIT.ST | BI | Lighting | - | Group status
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-03 | LTG-TENANT | LTG-TENANT.CMD | BO | Lighting | - | On/Off command | Time/calendar + astronomical (sunset) schedule
LCP-LTG | Common-area & facade lighting panel | DDC-LTG-03 | LTG-TENANT | LTG-TENANT.ST | BI | Lighting | - | Group status